## Slide 1: The LHC Cryogenics Availability Calculation Tool
8th International Workshop on Cryogenics Operation
4 – 7 June 2018
IHEP, CAS, Beijing, China
Laurent Delprat, Thomas Ytterdal
laurent.delprat@cern.ch

## Slide 2: Introduction Cryogenic conditions definition Cryogenic availability calculation tool architecture Statistics production Conclusion – Perspectives
OUTLOOK

## Slide 3
Compressor station
4.5 K refrigerator
1.8 K pumping unit (cold compressor)
Interconnection box
P1
P2
P3
P4
P6
P7
P8
P5
P18
B
B
A
A
B
B
A
A
LL
LL
LL
LL
HL
HL
HL
HL
A – upgraded ex-LEP cryo plant
B – new LHC cryogenic plant
LL – Low Load sector
HL – High Load sector
LHC Cryogenics
circumference  ~ 27 km,
constructed at ~ 100 m underground,
the accelerator ring inclination is 1.4 %
LHC cryogenics:
8 x 18 kW @ 4.5 K
1800 sc magnets
24 km & 20 kW @ 1.8 K
37 000 tons @ 1.9 K
130 tons of helium inventory
LHC Cryogenic System Architecture
Notes: Total for 8 sectors:
Compressors: 64
Turbines: 74
Cold Comp.: 28
Leads: 1’200
I/O signals: 60’000
PID loops: 4’000

## Slide 4
Set of cryogenic conditions:
to start powering (Cryo Start – CS)
to keep the magnets powered (Cryo Maintain – CM)…
… and in the end to allow for beams to circulate, and for physics production !
Cryogenic Conditions Definition
Notes: Oral introduction of the slide: availability of cryogenics is compulsory for the beam to circulate and for the production of physics => we shall then define what is “Cryogenics Availability”.
What’s more, and not presented here, LHC Cryogenics is integrated in AFT_LHC (“Availability & Fault Tracking Tool of LHC) – refer to B. Todd presentation.

## Slide 5
Set of cryogenic conditions:
to start powering (Cryo Start – CS)
to keep the magnets powered (Cryo Maintain – CM)
Example for magnet temperature
2.15 K
2.05 K
Magnet Temperature (K)
1.90 K
Cryo Maintain
Cryo Start
Operation Temperature
Perturbation
Temperature drift
Temperature decrease
Cryo conditions
back, towards nominal
Availability impacted!
Diagnose,
Repair (if needed),
Restart
Loss of
cryo conditions

## Slide 6
Set of cryogenic conditions:
to start powering (Cryo Start – CS)
to keep the magnets powered (Cryo Maintain – CM)
LHC operation schedule:
Beam start: Date D1
Beam end: Date D2
Technical stops: duration d (usually 2 to 3 times one week per year)
Due operation time: D = (D2 – D1) – d
Cryogenic downtime accounting
Cryo downtime: counted from CM lost to CS back = Dc
Does not take into account cryo faults originating from “Users” and “Technical Services”
Cryogenic Availability Calculation:
Cryogenic Availability: A = 1 – ( Dc / D )
How to calculate cryogenic availability

## Slide 7
Availability losses categorization

## Slide 8
Built using Microsoft Excel
Precision down to 1 minute
Requires manual extract of data from timber
Tracks Cryo Maintain losses
Current system for tracking LHC cryogenic availability

## Slide 9
Available at https://cscm.cern.ch
New system for tracking LHC cryogenic availability
Notes: Virtual machine in computing center
Python: programming language
Flask: Web framework for python
SQLAlchemy: used to communicate with database provided by the database on demand service at CERN
Bokeh: makes interactive javascript visualisations
Pandas and numpy: Mathematical libraries for python used for calculations

## Slide 10: CALS - CERN Accelerator Logging Service
The CERN-wide Accelerator Logging Service was born out of the LHC Logging Project, which was launched in 2001. The service first became operational in late 2003, and has since become what is considered to be a mission-critical service.
PyTimber
Written in Python 2.7/3.4.
Use jpype to interface with the excellent native Java CALS API.
How to get the data
Notes: CALS: data usually extracted using Timber
PyTimber: Python interface to get data from the CALS database. Also makes it possible to script extractions.
Next: workflow of script to extract data

## Slide 11
Timestamp Value
22-04-2017 10:14:01 0
22-04-2017 10:15:02 0
22-04-2017 10:17:05 1
Timestamp Value
22-04-2018 10:14:01 0
22-04-2018 10:17:05 1
Check for global CS loss
Check for global CM loss
Find Sector with CS loss
Find subsector for CS loss
Find equipment for CS loss
Find Sector with CM loss
Find subsector for CM loss
Find equipment for CM loss
Save to DB
Check data
Data OK
Log error
Fault in data
No CM loss
Check data
Log error
Fault in data or no data
Save to DB
Data OK
Check data
Log error
Fault in data or no data
Save to DB
Data OK
Check data
Fault in data
CM loss
Data OK
Check data
Log error
Save to DB
Data OK
Fault in data or no data
Check data
Log error
Save to DB
Data OK
Fault in data or no data
Check data
Fault in data or no data
Check data
Fault in data or no data
Save to DB
Data OK
Data OK
Wait 24h
Wait 30min
No loss
Loss in progress
Tool workflow
Notes: Workflow of script for collecting data
Data saved to database from the database on demand service at CERN
Values only stored on change, so repeating values is considered as an error
Block repeated throughout the script.

## Slide 12
List of global Cryo Start losses
Notes: List of global CS losses
Extra field filled if CM lost
Event 29th of April 2016: Weasel + 66kV transformer

## Slide 13
Weasel in LHC Point 8
Visualising a global Cryo Start loss
Notes: Global CS loss + all underlying losses
A bit difficult to read x-axis, but zoom and hover tool available
Next: closer look at the details for Sector 81 (by clicking the bar on the plot)

## Slide 14
Visualising details for one sector
Notes: Details for subsectors underlying the loss in Sector 81.
Next: Closer look at the loss in AR81

## Slide 15
Visualising details for one subsector
Notes: Details for all equipment losses underlying AR81
Conditions lost and regained several times during the period of the main loss
Next: Overview of how many times each equipment has been lost during the global loss

## Slide 16
Summary of all equipment losses during the global loss
Notes: Summary of which equipment have been lost, and how many times the condition have come and gone.
Zoom and hover tool available
Next: count all losses under the same global loss as one, and make an overview for the year.

## Slide 17
Summary of independent equipment losses in 2017
Notes: All losses under a global loss counted as one
Can be used as an early warning system to determine where we need to improve to avoid losing conditions.
Zoom and hover tool available

## Slide 18
Independent equipment losses in 2017 – zoom
Notes: Zoom of previous plot

## Slide 19
List of global Cryo Maintain Losses
Notes: - List of Global CM losses with categorization and sub categories

## Slide 20
Calculating the availability
Notes: Calculated availability
Daily CM, Cumulated CM availability, Cumulated Cryo, Cumulated CS

## Slide 21
Yearly plot of the cumulated availability
Notes: Yearly plot of the cumulated availability and daily availability
Comments can be added.

## Slide 22
LHC Cryo availability summary
from Run 1 to Run 2
Notes: - Summary of run time and CM categories since 2010

## Slide 23
CRYO
USERS
TECHNICAL SERVICES
Grouping the data by category
Notes: Grouped by category and sub category
Can be used to identify where we have lost the most time and what causes losses.
Can be used to signal to other departments where they need to put extra effort to reduce the cryo loss time due to their services.

## Slide 24
CryoMaintain Downtime Origins for 2017

## Slide 25
Easily available as a website
Precision down to 1 second
Automatically extracts data once a day
Less human interaction / chance of miscalculations
Tracks both Cryo Start and Cryo Maintain
Tracks all events during the loss of conditions
Advantages of the new system

## Slide 26
Conclusion – Perspectives
Run 1 operation used a fully manual tool for the calculation of availability
Thank you for your attention!
Questions ?
Run 2 operation started with the refurbishment of this old tool into a semi-automatized one, still giving some uncertainties in the results
Fully automatic calculation of the availability as well as online monitoring of the cryo start thresholds flips has been made possible with the implementation of this new tool
It will allow to use early-warning signals statistics for better anticipation and mitigation of failures when feasible