## Slide 1: Layout for the HEPEA
Speaker：Jing Hantao
Institute of High Energy Physics, Chinese Academy of Sciences (CAS)
Spallation Neutron Source Science Center
2020-12-12

## Slide 2: Contents
Layout of High-energy Proton Experimental Area (HPEA)
Infrastructure and room allocation in HPEA
Radiation shielding for HPEA
Common facililties and conditions

## Slide 3: Bird’s view of CSNS
Auxiliary area
Office area
Facility area
Test hall 1&2
Main substation
Support building
Exhaust and air-condition centers
Radiation protection building
2nd target station reserved
HPEA

## Slide 4: Layout of CSNS and High-energy Proton Experimental Area （HEPA）
Linac, 80 MeV@CSNS-I; 300 MeV@CSNS-II
RCS
1.6GeV, 25Hz
100 kW
1st target station
Proton beam parameters for Experimental Muon Source (EMuS)
Proton energy：1.6 GeV
Beam power：20 kW
Bunch number per pulse: 2
Repetition：1 Hz
Proton number per bunch：7.8 E13 ppp (protons per pulse)
High-energy Proton
Experimental Area(HPEA)
Notes: Negative hydrogen ion

## Slide 5: HEPEA Conceptual design rendering

## Slide 6: HEPEA in CSNS facility campus

## Slide 7: Infrastructure and room allocation in HEPEA
Exp. building：
3×25m×10.5m=788 m2
Extended tunnel：380 m2
Exp. hall： 49mX30m=1470 m2
Common equipment
room: 715 m2
Beam height：1.605 m
PBW
Exp. building (3 floors)：
User office
Labs
Preparation room
Detector and electronics room
Control room
Com. Equip. hall
ventilation
Supp. power
Water cool system

## Slide 8: Supply power and ground wire
Common electric power （450 kW）
For Lights, cranes, air-condition and ventilation and so on；
Beamline equipment electric power（1500 kW）
For vacuum pumps, magnet and so on；
Clear electric power (Low noise) （100 kW）
For detector , electronics，DAQ server and control system et al.
Ground resistance（independent)：0.5-1.0 Ω

## Slide 9: Cool water
For magnet and target shielding
Deionized water;
water-collecting well;
Water volume: 80m3/h;
Tap water；
Phase | Thickness of carbon target | Energy deposition | Max. tempture
Simplified-scheme | 100mm | 635.5W | 704deg.
Baseline scheme | 10mm | 63.55 W | 238deg.
 | 300mm | 1906.5 W | 880deg.

## Slide 10: Ventilation
Extended tunnel
Same to operation mode of RTBT
Exp. hall
No activated air and loop with a period of 2 hour
Independent air condition
Parameter of ventilation:
Tunnel and experimental hall:
Environment temperature and humidity: 25±2 degree and 65±5%
Electronics and DAQ system:
Environment temperature and humidity: 23±2 degree and 65±5%
Extended tunnel
Exp. hall
Exp. building
Common
Equipment
hall

## Slide 11
Cryogenic system
High-pressure He gas tank
Compressor & Oil removing device
Cryogenic hall
Cold box & He Dewar
Cryogenic platform
Cryogenic hall with area of 60 m2：high-pressure He gas tank, compressor, Oil removing device
A platform with 40m2 for Cold box & He Dewar
Liquid He surrounding by 80 k He gas is sent to SC cryogenic box
Cryogenic boxes
Target station
Straight section 1
Straight section 2

## Slide 12: Radiation shielding and protection

## Slide 13: Target area and dump
Shielding limited value:
<1mSv/h (30cm from surface of equipment) after 4 hours with 100 days operation.
<2.5 μSv/h in experimental hall
mSv/h

## Slide 14: Radiation shielding for baby scheme
mSv/h
About 3m thickness for front shielding wall

## Slide 15: Shielding for baseline
Dose-EQ after 4 hours with 100 days operation(mSv/h）
Prompt dose-EQ（mSv/h）
About 1.6-m thickness of the divided wall on right side;

## Slide 16: Thanks