## Slide 1
CEPC Cryogenic System and Technology Development
Rui Ge
12-16 June 2023, Hongkong, CEPC Accelerator TDR International Review

## Slide 2: Content
CEPC Cryogenic System Brief Introduction
Cryogenic system for the SRF
Cooling Scheme Optimization and Process Calculation
Development of key equipment and technology
Platform of Advanced Photon Source Technology （PAPS）
Cryogenic system for SC magnets
Summary

## Slide 3: CEPC Cryogenic System Brief Introduction
  Booster ring:
1.3 GHz 9-cell cavities, 96 cavities
12 cryomodules
3 cryomodules/each station
Temperature: 2K
  Collider ring:
650MHz 2-cell cavities, 336 cavities
56 cryomodules
14 cryomodules/each station
Temperature: 2K
  IR magnets:
4 IR magnets,
Temperature: 4.5K
Detectors:
2 detector magnets
Thermosiphon cooling

## Slide 4: CEPC Cryogenic System Brief Introduction
  30 MW Higgs:
Collider: 192 650 MHz 2-cell cavities in 32 modules (6 cav / CM)
Booster: 96 1.3 GHz 9-cell cavities in 12 modules (8 cav / CM)
  50 MW Higgs:
Collider: add 24 modules, in total 56 650 MHz modules
Booster: 96 1.3 GHz 9-cell cavities in 12 modules (8 cav / CM)
Cryomodules for Higgs 30 / 50 MW

## Slide 5: CEPC Cryogenic System Brief Introduction
IDEA detector
LTS Solenoid
HTS Solenoid
LTS Solenoid ：
Solenoid located outside calorimeter
Inner diameter 7.2 m, length 7.4 m
Central field：3 T
Superconductor：NbTi
Operation temperature：4.2 K
HTS Solenoid ：
Solenoid located inside calorimeter/less material
Inner diameter 4 m, length 6 m
Central field：2 T
Superconductor：YBCO
Operation temperature：20 K
From Zhu Ying-shun
Zhu Zian，Wang Meifen
SC magnets cryogenic system overview

## Slide 6: Content
CEPC Cryogenic System Brief Introduction
Cryogenic system for the SRF
Cooling Scheme Optimization and Process Calculation
Development of key equipment and technology
Platform of Advanced Photon Source Technology R&D（PAPS）
Cryogenic system for SC magnets
Summary

## Slide 7: Flow chart of SRF CDR Scheme
11000
11000
11000
5000
5000
Compressor group
Cold Box
Main Distribution
Valve Box
Dewar
11000
8000
5000
5000
10
Cryomodules
11000
11000
11000
117000
24000
224000
2K valve boxes
加速器中心低温组
14 cryomodules, 6×650MHZ 2-cell cavities each
Collider Ring
3 cryomodules, 8×1.3GHZ 9-cell cavities each
Booster Ring
Auxiliary-tunnel
80000
50MW

## Slide 8: Estimated heat loads for SC cavities-CDR Scheme
Higgs Mode 50MW | Unit | Collider |  |  | Booster |  | 
 |  | 40-80K | 5-8K | 2K | 40-80K | 5-8K | 2K
Predicted static heat load per cryomodule | W | 300 | 60 | 12 | 140 | 20 | 3
Cavity dynamic heat load per cryomodule | W | 0 | 0 | 153.59 | 0 | 0 | 13.98
HOM dynamic heat load per cryomodule | W | 20 | 12 | 2 | 2 | 1 | 1
Input coupler dynamic heat load per cryomodule | W | 60 | 40 | 6 | 40 | 3 | 0.4
Module dynamic heat load | W | 80 | 52 | 161.59 | 42 | 4 | 15.38
Each Module total heat load | W | 380 | 112 | 173.59 | 182 | 24 | 18.38
Cryomodule number | - | 56 | 56 | 56 | 12 | 12 | 12
EVB heat loss | W | 50 | 10 | 10 | 50 | 10 | 10
EVB number | - | 40 | 40 | 40 | 12 | 12 | 12
MDVB heat loss | W | 50 | 30 | 30 | 50 | 30 | 5
MDVB number | - | 4 | 4 | 4 | 4 | 4 | 4
Total cryogenic transfer line length | m | 1924 | 1924 | 1924 | 536 | 536 | 536
cryogenic transfer line heat loss per meter | W/m | 2 | 0.5 | 0.3 | 2 | 0.5 | 0.3
Total cryogenic transfer line heat loss | W | 3848 | 962 | 577.2 | 1072 | 268 | 160.8
Total heat load | kW | 27.328 | 7.754 | 10.81824 | 4.056 | 0.796 | 0.52136
Total predicted mass flow | g/s | 82.42 | 152.26 | 373.72 | 13.34 | 12.73 | 18.324
Overall net cryogenic capacity multiplier |  | 1.54 | 1.54 | 1.54 | 1.54 | 1.54 | 1.54
4.5K equiv. heat load with multiplier | kW | 3.16 | 10.80 | 53.32 | 0.47 | 1.11 | 2.58
4.5K equiv. heat load with multiplier | kW | 67.29 |  |  | 4.15 |  | 
Total 4.5K equiv. heat load with multiplier | kW | 71.44 |  |  |  |  | 

## Slide 9: Flow chart of SRF TDR Scheme
3 cryomodules, 8×1.3GHZ 9-cell cavities each
Booster Ring
14 cryomodules, 6×650MHZ 2-cell cavities each
Collider Ring
11000
11000
11000
5000
5000
Compressor group
Cold Box
Main Distribution
Valve Box
Dewar
11000
8000
5000
5000
10
Cryomodules
11000
11000
11000
117000
24000
2K valve boxes
2K valve boxes
Smaller diameter

## Slide 10: Estimated heat loads for SRF TDR Scheme
Higgs Mode 50MW | Unit | Collider |  |  | Booster |  | 
 |  | 40-80K | 5-8K | 2K | 40-80K | 5-8K | 2K
Predicted static heat load per cryomodule | W | 300 | 60 | 12 | 140 | 20 | 3
Cavity dynamic heat load per cryomodule | W | 300 | 60 | 118.2 | 0 | 0 | 44.8
HOM dynamic heat load per cryomodule | W | 20 | 12 | 2 | 20 | 6 | 1
Input coupler dynamic heat load per cryomodule | W | 60 | 40 | 6 | 40 | 3 | 0.4
Module dynamic heat load | W | 380 | 112 | 126.2 | 60 | 9 | 46.2
Each Module total heat load | W | 680 | 172 | 138.2 | 200 | 29 | 49.2
Cryomodule number | - | 40 | 40 | 40 | 12 | 12 | 12
EVB heat loss | W | 50 | 10 | 10 | 50 | 10 | 10
EVB number | - | 40 | 40 | 40 | 12 | 12 | 12
MDVB heat loss | W | 50 | 30 | 30 | 50 | 30 | 5
MDVB number | - | 4 | 4 | 4 | 4 | 4 | 4
Total cryogenic transfer line length | m | 1000 | 1000 | 1000 | 300 | 300 | 300
cryogenic transfer line heat loss per meter | W/m | 2 | 0.5 | 0.3 | 2 | 0.5 | 0.3
Total cryogenic transfer line heat loss | W | 2000 | 500 | 300 | 600 | 150 | 90
Total heat load | kW | 31.4 | 7.9 | 6.348 | 3.8 | 0.738 | 0.8204
Total predicted mass flow | g/s | 82.42 | 152.26 | 373.72 | 13.34 | 12.73 | 18.324
Overall net cryogenic capacity multiplier |  | 1.54 | 1.54 | 1.54 | 1.54 | 1.54 | 1.54
4.5K equiv. heat load with multiplier | kW | 3.63 | 11.01 | 31.29 | 0.44 | 1.03 | 4.05
4.5K equiv. heat load with multiplier | kW | 45.93 |  |  | 5.52 |  | 
Total 4.5K equiv. heat load with multiplier | kW | 51.45 |  |  |  |  | 
Four individual refrigerators (4 × 15kW@4.5K) will be employed for the CEPC cavity cryogenic system.

## Slide 11: Layout of CEPC cryogenic hall
Helium purifier
High pressure helium cylinders
10*100m3 helium gas
Pressure vessels
4*50m3 LN2 Storage Tanks
Recycle screw compressors
Piston compressors
Electrical control system
Helium gas bag

## Slide 12: Layout of CEPC cryogenic system for SRF
Warm equipment on the ground:
compressor hall, helium gas tanks
Cold equipment under the ground
Beam tunnel
Gallery tunnel
Refrigerator
cryomodules
2K valve boxes
Shaft
Cryogenic transfer line

## Slide 13: Tunnel cross section

## Slide 14: cryogenic system process flow diagram in the SRF system
5K@3bara supercritical helium subcooled to 4.5K, and then through 2K JT heat exchanger reduced to 2.2K@3bara.
2.2K@3bara helium throttled by JT valve to produce the 2K super flow helium.
40-80K loop to cool down the cryomoduls’ thermal shield.
5-8K loop to cool down the coupler.

## Slide 15: Booster cryomodules for String

## Slide 16: Collider cryomodules for String

## Slide 17: Process calculation
Scheme1
Scheme2
0.15W/m single loop transfer line heat loss
Collider: after modified, Smaller diameter

## Slide 18: 40K~80K TS calculation
Total main supply pipe length is 430 meters, and the heat loss per meter is 2.0 W.
The mass flow of liquid helium needs to be provided by the refrigerator is no less than 26.88 g/s .
Main supply pipe sizes: collider- Di=30.8 mm, Booster-Di=14.6 mm.
Main return gas pipe sizes: collider- Di=38.8 mm, Booster-Di=18.8 mm.
Branch supply pipe sizes: collider- Di=18.8 mm, Booster-Di=14.6 mm.
Branch return gas pipe sizes: collider- Di=18.8 mm, Booster-Di=14.6 mm.

## Slide 19: 5K~8K TS calculation
Total main supply pipe length is 430 meters, and the heat loss per meter is 0.5 W.
The mass flow of liquid helium needs to be provided by the refrigerator is no less than 51.21 g/s .
Main supply pipe sizes: collider- Di=30.8 mm, Booster-Di=14.6 mm.
Main return gas pipe sizes: collider- Di=85 mm, Booster-Di=23.8 mm.
Branch supply pipe sizes: collider- Di=18.8 mm, Booster-Di=14.6 mm.
Branch return gas pipe sizes: collider- Di=18.8 mm, Booster-Di=14.6 mm.

## Slide 20: Development of the key equipment and technology
Large refrigerator
1.3GHz cavity cryomodule
650MHz cavity cryomodule
KW JT heat exchanger
Advanced control strategy

## Slide 21: Key equipment and technology
Large refrigerator
Technical supported by FULL CRYO Company and TIPC, CAS
2.5 kW @4.5K or 500W @2K refrigerator have passed test and will be installed in CIADS campus for the long time running to verify the stability.
The CAS pilot project for the 10 kW @4.5K or 15 kW @4.5K (required for CEPC) has been approved, and it is expected to be developed and fully prepared for CEPC in the next few years.

## Slide 22: Key equipment and technology
Large refrigerator
Other parameters | Precooled by Turbin expanders | Precooled by liquid nitrogen
The consumption of the Liquid Nitrogen | 0g/s (0L/h) | 428.7g/s(2043L/h)
Gas flow for precooling | 100g/s | 0g/s
Gas flow（g/s） | 1668g/s | 1551g/s
Power Consumption（KW） | 3935.13 | 3721.3
Parameters | The high pressure compressor | The medium pressure compressor | The low pressure compressor
Gas flow (g/s)* | 1668.00 | 862.80 | 230.7
Pressure of the inlet (bara) | 4.05 | 1.05 | 0.40
Pressure of the outlet (bara) | 18.54 | 4.05 | 1.05
Adiabatic efficiency （%） | 85 | 85 | 85
Power consumption (kW) | 2568 | 1155 | 196.3
Parameters of the refrigerator
Parameters of the cold compressor

## Slide 23: 1.3GHz cavity Cryomodule

## Slide 24: 1.3GHz cavity Cryomodule

## Slide 25: 1.3GHz cavity Cryomodule
Endcap
超导腔模组
Feedcap
2K测试阀箱

## Slide 26: 1.3GHz cavity Cryomodule
Cooling scheme for the 1.3 GHz 9-cell SRF cavity module

## Slide 27: 1.3GHz cavity Cryomodule
Unsteady-state simulation for the 1.3GHz cryomodule cooldown process

## Slide 28: 1.3GHz cavity Cryomodule

## Slide 29: 1.3GHz cavity Cryomodule

## Slide 30: 650MHz cavity Cryomodule
Including six 2-cell 650 MHz superconducting cavities, six high power couplers, six mechanical tuners and two HOM absorbers
Cryomodule performance |  | Specification
Number of leakage | He →insulation | 0
 | He →beam pipe | 0
 | Insulation →coupler | 0
 | Insulation →beam pipe | 0
 | Coupler →beam pipe | 0
Alignment x/y inside (Cavities) |  | ±0.5mm
Alignment z inside |  | within 2 mm
Coupler antenna design z |  | within 2 mm
Six 2-cell Cavities Cryomodule | 
Overall length(flange to flange, m) | 8.0
Diameter of Vacuum vessel ,m | 1.3
Beamline height from floor, m | 1.5
Cryo-system working temperature, K | 2
Number of 200-POST | 6

## Slide 31: 650MHz cavity Cryomodule
Prototype of 650MHz cryomodule with 2* 2cell cavities have been installed in PAPS tunnel and past the cryogenic test.

## Slide 32: 650MHz cavity Cryomodule
a) 260K b) 220K c) 180K
d) 140K e) 100K f) 60K
g) 40K h) 20K
The cooling rate of the superconducting cavity needs to be strictly controlled, and a three-dimensional flow field non-stationary numerical simulation of the cooling process of the 650 2-cell superconducting cavity is performed.
A certain simulation basis is laid for the subsequent automatic cooling.
Global velocity distribution
Non-stationary analysis of superconducting cavity cooling process

## Slide 33: 650MHz cavity Cryomodule
BTCM cooldown
BTCM: 100.7W@2K
Level
Pressure
Temperature
Mass flow
BTCM 2K stable operation
Pressure 31mbar±10Pa
Temperature 2K±0.02K
Cryogenic capacity test, 300W@2K return gas flow rate

## Slide 34: KW JT heat exchanger
Designing & Verification
NSGA-II Optimization
For CEPC 2kW@2K cryogenic system, the kilo-watt scale heat exchanger project began in 2022.
2022.05-2022.10 Basic Design and Optimization.
CFD Designing Reslut

## Slide 35: KW JT heat exchanger
Checking Thickness
Build Up
Before Brazing
After Product
2022.10-2023.05 Manufacturing and Quality Detection.
Leakage Detection

## Slide 36: KW JT heat exchanger
2023.01-2023.06 Cryogenic experiment design and similarity experimentdesign.
Similarity Experiment Dewar
and Inner structure
The similarity experiment will hold in 2023.7
and cryogenic experiment will hold in 2023.12

## Slide 37: Platform of Advanced Photon Source Technology R&D （PAPS）
先进光源技术研发与测试平台
Platform of Advanced Photon Source Technology R&D (PAPS)
加速器分平台
Accelerator platform
X射线分平台
X-Ray platform
超导高频系统 RF system
精密磁铁系统 Magnet technology
低温系统 Cryogenic system
束流测试系统 Beam test
X射线光学系统 X-ray optics
X射线探测系统 X-ray detection
X射线应用系统 X-ray application
“Platform of Advanced Photon Source Technology R&D”, The goal of the PAPS project is to provide a good foundation and condition for R&D, engineering testing and verification for the high energy phone source (HEPS) project to be completed on schedule and to achieve the expected design target.
Budget: 500M CNY funded by Beijing Gov.
Construction: 2017.5-2021.6

## Slide 38
SRF building
Cryogenic building
Magnet building
Beam test building
X-ray building

## Slide 39: Process Flow Diagram of PAPS Cryogenic System
Pump Group
Helium Refrigerator
MDVB
Beam Test Stand
Horizontal Test Stand
Single Cavity Cryomodule HT
Vertical Test 1
Vertical Test 2
Vertical Test 3

## Slide 41: PAPS cryogenic hall

## Slide 42
PAPS RF hall-cold box

## Slide 43: PAPS RF hall-vertical test stand

## Slide 44: PAPS RF hall-single cavity horizontal test stand
Length: 3800
Height: 3200
Diameter:1400
Fast cooling down test
Test two cavities at a time
Test cavity performance at 2K
Test and check key equipment of SC cavity such as tuner, power coupler, HOM coupler etc.

## Slide 45: PAPS RF hall-cryomodule horizontal test stand

## Slide 46: Beam test facility

## Slide 47: Content
CEPC Cryogenic System Brief Introduction
Cryogenic system for the SRF
Cooling Scheme Optimization and Process Calculation
Development of key equipment and technology
Platform of Advanced Photon Source Technology R&D（PAPS）
Cryogenic system for SC magnets
Summary

## Slide 48: Detailed flow chart for the IR Cryostat
Compressor
Cold box
Dewar
Main Distribution Valve Box
Helium circulating system 1
Helium circulating system 2
Cryostat 1
Cryostat 2
IP collision point

## Slide 49: Estimated heat loads for SC IR magnets-updated
 |  | 4.5K main loop |  |  | Thermal Shielding 40~80K |  | 
Name | Unit | No. | Heat load for each | Heat load | No. | Heat load for each | Heat load
IR SC magnet | W | 4 | 30 | 120 |  |  | 
Valve Box of IR SC magnet | W | 4 | 30 | 120 |  |  | 
Current lead of IR SC magnet | g/s | 4 | 0.8 | 3.2 |  |  | 
Main distribution valve box | W | 4 | 50 | 100 |  |  | 
Cryogenic transfer-line | W | 100 | 0.3 | 30 | 100 | 1.5 | 150
Total heat load @4.5K | W |  |  | 370 |  |  | 150
Total heat load @4.5K including current lead | W |  |  | 370W+3.2g/s |  |  | 150
Total heat load @4.5K | W |  |  | 432 |  |  | 150
Coefficient |  |  |  | 1 |  |  | 0.05
Total heat load @4.5K | W |  |  | 432 |  |  | 7.5
Total equiv. heat load @4.5K | W | 439 |  |  |  |  | 
Total equiv. heat load @4.5K with multiplier 1.5 | W | 659 |  |  |  |  | 

## Slide 50: Mechanical structure of IR Cryostat

## Slide 51: Thermal dynamics simulation
Research on the flow and heat transfer of helium in the narrow channels.
Choose the appropriate cooling method.

## Slide 52: summary
Previous CDR and TDR works have laid a good foundation for the further design.
For the CEPC cryogenic system TDR design, relevant aspects have been considered , including process scheme, layout, and key equipment design.
For the RF side, scheme 2 can reduce construction expenses, and has the advantage of low heat loss and easier transfer line construction and flexible maintenance.
For the IR magnets, the preliminary process calculation has been completed. Further detailed design is ongoing.
Several key technologies (JT heat exchanger platform/cryo-circulating pump/multi-channel Transfer line test platform/Virtual system establishment and automatic control strategy research) are considered.

## Slide 53
Thanks for Your Attention！