## Slide 1
Cost of CEPC auxiliary facilities
Huang Jinshu
12-16. June. 2023, Hongkong, CEPC Accelerator TDR International Review

## Slide 2: Content
Introduction
Auxiliary facilities
  Electric engineering
  Cooling water system
  HVAC
  Compressed air system
  Fire protection and water supply
Summary

## Slide 3
Electric engineering
Power consumption of CEPC
  Higgs

## Slide 4
Power supplies and schemes
  220kV/110kV Master substation
    2 substations
    Rated capacity of transformer: 2*210MVA (220/110kV/10kV).
  110kV/10kV step-down substations
    4 substations respectively located in IP1~IP4.
    Total rated capacity of transformer: 680MVA.
  10kV step-down substations
    132 substations
      Surface 10kV loop : 36
      Underground 10kV loop ：96 substations (10/0.4kV ) along the ring tunnel.
    Total rated capacity of transformer: 328.3MVA.
Electric engineering

## Slide 5
  10kV step-down substations
Rated capacity of 10kV/0.4kV transformer: 328.3MVA
 | Subsation Name | Num. of Subsation | Diagram of 10kV | Circuit Num. | Load of 10kV Subsation | Scale of Substation（0.4kV） | Location of Subsation
1 | IP1，IP3 10kV Substiaon | 6 | Single Bus section | 3 incoming 24 outgoing | 28.8MW(10kV） 2.5MW（0.4kV） | 2x3150kVA | Nearby 1# &2#RF Power Tunnel 1#~2# Power Hall
2 | IP2，IP4 10kV Substiaon | 2 | Single Bus 2 section | 2 incoming 26 outgoing | 3.8MW(10kV) 4.6MW(0.4kV) | 4x2000kVA | 1# & 2# IR Equipment Hall 3#~4# Power Hall
3 | LSS1~LSS4 10kV Substiaon | 4 | Single Bus 2 section | 3 incoming 10 outgoing | 3.8MW(10kV) 2.7MW(0.4kV) | 2x2500kVA | 5#~8# Power Hall
4 | LINAC 10kV Substiaon （24# ） | 1 | Single Bus 2 section | 2 incoming 10 outgoing | 6MW(10kV) 4.5MW | 2x2500kVA | LINAC Gallery
5 | 1#~23# grounding 10kV Substiaon | 23 | Single Bus 2 section | 2 incoming 10 outgoing | 1MW | 2x1250kVA | Surface Substaion
6 | 1#~96# Auxiliary Tunnel | 96 | Single Bus 2 section | 2 incoming 2 outgoing | 0.8MW | 2x1000kVA | Auxiliary Tunnel
Electric engineering

## Slide 6
Electric engineering

## Slide 7
Key requirements and parameters
  Total heat load : 280.48MW
  Total flow rate of LCW: 31982m3/h
  Total flow rate of CTW: 48234m3/h
  DW：Single DW unit can produce 3~5t/h deionized water with the effluent quality meets the following standards.
  Storage capacity of low-level radioactive wastewater ：5100m3
  Centralized water supply station: 18
Colling water system

## Slide 8
Subsystem partition
  56 closed-loop of LCW
  20 CTW subsystems
  18 DW subsystems
The division of LCW subsystem depends on the demand of water-used equipment:
  Temperature
  Pressure,
  Water quality,
  Radiation dosage
  Location
Subsystem partition of Cooling water system
Colling water system

## Slide 9
Colling water system
Cost of Subsystem partition
Take accelerating tube and waveguide circuit as an example.

## Slide 10
Colling water system

## Slide 11
Estimated cooling loads of HVAC
  Ring tunnel: 14MW
  Service buildings: (200W/m2) 28MW
  Total: 42MW
Coolant for air conditioning: chilled water
Design parameter | Unit | quantity
Total cooling load | MW | 42
Total chilled water flow rate | m3/h | 7223
Total cooling tower water flow rate | m3/h | 8667
Total capacity of cooling towers | MW | 50
Heating Ventilation and Air Conditioning
Air-conditioning system in tunnel
  The ring tunnel is divided into 32 independent sections.
  Each shaft serves as a ventilation and exhaust channel for the underground main ring tunnel, and a ventilation pipe and a smoke exhaust pipe are arranged therein.

## Slide 12
Heating Ventilation and Air Conditioning

## Slide 13
Compressed air system
Key requirements and parameters
    Centralized compressed air station: 18
  -- Operating Pressure： 0.6~0.8MPa
  -- Single Plant Capacity：10Nm3/h
  -- Particle Removal Efficiency: ≥99.97%
  -- Pressure Dewpoint Temp.: -40℃
  -- Oil Content: ≤0.01ppm
    Centralized air cooling station: 2

## Slide 14
Fire protection and water supply

## Slide 15
Summary
    The cost of CEPC auxiliary facility are compiled according to the design scheme in the TDR.
    Reserves and any unforeseen installation costs are charged at a rate of 10%.
    In recent years, the prices of major materials have fluctuated greatly, which has brought great difficulties to the preparation of the cost.

## Slide 16: Thank you for your attention!

## Slide 17
Copper-2018
Copper-2022
Copper-2020
Copper-2021
Back-up

## Slide 18
Back-up
NI-2018
NI-2022
NI-2021
NI-2020