## Slide 1
CEPC MDI EDR cryomodule design progress
Xiangzhen Zhang, Xiaochen Yang
On behalf of cryogenics group，Institute of High Energy Physics(IHEP)
2024.08.23
The 2024 CEPC Mechanical Workshop, Luoyang, Henan

## Slide 2: Content
Introduction
Cryogenic scheme of the cryostat
Structural design of the cryostat
Calculation and simulation
Current leads design
Summary and plan

## Slide 3
  Introduction
In CEPC, there are two combined-function Superconducting magnets in MDI
Each combined-function magnet includes double aperture high gradient quadrupole (Q1a, Q1b, Q2) and anti-solenoid, around each side of the IP point.
The cryostat is used to provide the cryogenic environment for SC magnets, which is below 5.0 K.
From Yingshun Zhu
ITEM | Q1a | Q1b | Q2 | Anti-solenoid
Central field gradient (T/m) | 142.3 | 85.4 | 96.7 | 
Cooling type | LHe | LHe | LHe | LHe
Operating current (A) | 780 | 650 | 770 | 1300
Magnetic storage energy (KJ) | 11.5 | 11 | 33.2 | 630
Cross section parameter (mm) | Φ40~61 | Φ52~78 | Φ62~88 | 100 sections
Magnet length (m) | 1.21 | 1.21 | 1.53 | 5.1
Net weight (Kg) | 25 | 32 | 43 | 302
Total weight of magnets (Kg) |  |  |  | 402

## Slide 4
  Introduction
Design and optimization of the structure.
Heat and mass transfer of the cryostat.
PI＆D of the cryogenic system.
Scheme of the current leads.
Some other problems.
From Yingshun Zhu
Works for the cryostat

## Slide 5
  Introduction
KEK and FCC
The length is approximately 3.3 m, and diameter is 1.1 m.
The weight of the magnet cryostat is 1570kg.
It is cooled by subcooled liquid helium at the pressure of 0.16MPa.
The length is approximately 3.36 m initially, and 6.24 m for second option.
It is cooled by superfluid helium He∥. (2.0 K)

## Slide 6
Superconducting magnets are immersed in the helium tank for the low temperature.
One thermal shield is set for the heat interruption from the ambient temperature.
The shield is extended between the helium tank and the beam chamber.
The 4K cold mass is cooled by supercritical or subcooled helium, and the shield is by liquid nitrogen.
Cryogenic scheme of the cryostat
Cryostat scheme

## Slide 7
Conventional helium cooling scheme: Liquid helium is directly provided by helium refrigerator. The flow rate is limited by the refrigerator. Liquid helium can be subcooled or supercritical type.
Helium circulation cooling scheme: A closed helium circulation is established depending on a pump. The flow rate can be increased largely. The system will be complex.
Superfluid helium(HeⅡ): Perfect cooling uniformity; Stable pressure; Higher magnet current; Higher cost.
Cryogenic scheme of the cryostat
Cooling system

## Slide 8
1985mm
1915mm
2885mm
Q1a
Q1b
Q2
Anti-solenoid
Structural design of the cryostat
Support of SC magnet
The superconducting magnets Q1a,Q1b and Q2 are supported on the inner wall of the solenoid.
The anti-solenoid is supported by a ring on the inner wall of the helium tank.
Vacuum
Thermal shield
LHe tank
Support
Anti-solenoid
Q1a
Beam chamber
Notes: 标注尺寸

## Slide 9
Outer cylinder of helium tank
Fluid domain
inlet
outlet
Cooling flow: One-way in and out
Without considering the magnetic support structure:
Heat conduction of support is 13.68 W; Heat flux of thermal radiation is 0.1 W/m2;
Helium inlet flow is 3.0 bar@4.2 K.
Chart: Coil number of anti-solenoid
| 1 | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
4.0 g/s | 4.39 | 4.71 | 16.6 | 11.95 | 10.07 | 13.438 | 12.49 | 10.25 | 9.04 | 8.59 | 6.8 | 5.34 | 4.86 | 4.74 | 4.52 | 4.56 | 4.69 | 4.84 | 4.78
6.0 g/s | 4.295 | 4.297 | 12.81 | 9.592 | 8.624 | 9.58 | 9.492 | 8.457 | 7.56 | 7.25 | 6.37 | 5.49 | 4.65 | 4.61 | 4.39 | 4.36 | 4.37 | 4.46 | 4.54
8.0 g/s | 4.29 | 4.29 | 7.26 | 8.39 | 8.02 | 11.46 | 11.12 | 9.14 | 7.63 | 6.45 | 5.53 | 4.82 | 4.47 | 4.38 | 4.32 | 4.3 | 4.31 | 4.32 | 4.38
12.0 g/s | 4.262 | 4.262 | 8.301 | 6.94 | 6.31 | 5.96 | 6.18 | 5.83 | 5.5 | 5.26 | 4.78 | 4.42 | 4.4 | 4.42 | 4.35 | 4.34 | 4.33 | 4.32 | 4.43
Calculation and simulation
Cooling of anti solenoid
Not feasible！

## Slide 10
Cooling flow: Outer single-layer flow channel ：
Chart: Coil number of anti-solenoid
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
2g/s | 4.9018 | 4.9282 | 4.9373 | 4.9266 | 4.926 | 4.9229 | 4.9462 | 4.9511 | 4.9833 | 4.9767 | 5.0021 | 4.9386 | 4.9673 | 4.9463 | 4.9375 | 4.9436 | 4.9458 | 4.9556 | 4.972 | 5.0009
4g/s | 4.6213 | 4.6405 | 4.6486 | 4.6389 | 4.6412 | 4.6358 | 4.6493 | 4.6539 | 4.6883 | 4.6817 | 4.7157 | 4.6507 | 4.7019 | 4.6544 | 4.649 | 4.6522 | 4.6551 | 4.6621 | 4.6685 | 4.6788
6g/s | 4.5924 | 4.6094 | 4.6143 | 4.6077 | 4.6109 | 4.603 | 4.6196 | 4.6153 | 4.6559 | 4.6486 | 4.7045 | 4.6507 | 4.6786 | 4.6373 | 4.6307 | 4.6476 | 4.645 | 4.6522 | 4.6507 | 4.6525
10g/s | 4.4571 | 4.471 | 4.4757 | 4.4682 | 4.47 | 4.4629 | 4.4767 | 4.4715 | 4.5003 | 4.4955 | 4.5597 | 4.5019 | 4.547 | 4.4848 | 4.4695 | 4.4848 | 4.4896 | 4.4946 | 4.4868 | 4.4709
Chart: Coil number of anti-solenoid
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
2g/s | 4.6856 | 4.6678 | 4.6984 | 4.7036 | 4.7072 | 4.711 | 4.714 | 4.7202 | 4.734 | 4.7332 | 4.758 | 4.7424 | 4.7473 | 4.7652 | 4.7707 | 4.7721 | 4.7678 | 4.7749 | 4.7837 | 4.7986
4g/s | 4.4286 | 4.4316 | 4.4506 | 4.4592 | 4.4631 | 4.4701 | 4.4665 | 4.4708 | 4.4883 | 4.4882 | 4.5134 | 4.4833 | 4.504 | 4.5127 | 4.5204 | 4.5222 | 4.5155 | 4.5194 | 4.5257 | 4.5321
6g/s | 4.4004 | 4.4041 | 4.4091 | 4.41 | 4.4199 | 4.4211 | 4.4254 | 4.4275 | 4.4478 | 4.4484 | 4.4884 | 4.4452 | 4.4681 | 4.4731 | 4.4827 | 4.4916 | 4.4834 | 4.4857 | 4.4869 | 4.4931
10g/s | 4.3302 | 4.3328 | 4.3358 | 4.3342 | 4.3412 | 4.338 | 4.3468 | 4.3456 | 4.3607 | 4.3566 | 4.3936 | 4.3545 | 4.3801 | 4.3734 | 4.375 | 4.385 | 4.3844 | 4.386 | 4.3807 | 4.3802
Chart: Helium flow channel（single-layer）
| 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 20
进出口压差Pa | 0.8413 | 3.3359 | 7.4465 | 13.2656 | 20.9472 | 29.6841 | 40.5507 | 53.136 | 82.7403
Temperature distribution of the outer cylinder of the helium tank: 3bar@4.2K 10g/s
Calculation and simulation
inlet
outlet
Cooling of anti solenoid

## Slide 11
Optimized helium channel
Quadrupole flow channel:
Anti-solenoid flow channel :
Inner and outer double flow channel design：
Minimum gap is 4mm
Minimum gap is 2mm
inlet
outlet
inlet
outlet
Calculation and simulation

## Slide 12
Comparison of single-layer and double-layers cooling channels ：
A double-layers flow channel is more effective for cooling superconducting magnets compared to a single-layer flow channel, especially when the helium flow rate is low ；
Some other advantages, including the heat management, quench recovery or magnet cooling time.
Chart: Coil number of anti-solenoid
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
2g/s Single flow channel design Anti-solenoid Peak temperature | 4.9018 | 4.9282 | 4.9373 | 4.9266 | 4.926 | 4.9229 | 4.9462 | 4.9511 | 4.9833 | 4.9767 | 5.0021 | 4.9386 | 4.9673 | 4.9463 | 4.9375 | 4.9436 | 4.9458 | 4.9556 | 4.972 | 5.0009
10g/s Single flow channel design Anti-solenoid Peak temperature | 4.4571 | 4.471 | 4.4757 | 4.4682 | 4.47 | 4.4629 | 4.4767 | 4.4715 | 4.5003 | 4.4955 | 4.5597 | 4.5019 | 4.547 | 4.4848 | 4.4695 | 4.4848 | 4.4896 | 4.4946 | 4.4868 | 4.4709
2g/s Double flow channel design Anti-solenoid Peak temperature | 4.6173 | 4.6526 | 4.6609 | 4.6415 | 4.6379 | 4.6348 | 4.663 | 4.6674 | 4.7316 | 4.7112 | 4.7102 | 4.6389 | 4.6693 | 4.6463 | 4.6367 | 4.6397 | 4.6417 | 4.6514 | 4.6704 | 4.7153
10g/s Double flow channel design Anti-solenoid Peak temperature | 4.441 | 4.4609 | 4.4646 | 4.4531 | 4.4536 | 4.4477 | 4.4703 | 4.4697 | 4.5207 | 4.5111 | 4.5565 | 4.497 | 4.5315 | 4.4571 | 4.4533 | 4.467 | 4.4697 | 4.4763 | 4.4689 | 4.4536
Calculation and simulation
inlet
outlet
Cooling of anti solenoid

## Slide 13
Calculation and simulation
Cooling of quadrupole coils
Helium flows into the inner channel and out from the outer channel.
Q1-A
Q1-B
Q2
Thermal radiation 0.2 W/m2
Thermal radiation 0.2 W/m2
Surface emissivity:
Thermal radiation 17.055 W/m2
Inlet helium state:
3.0bar@4.5K
(Supercritical helium)
Fluid pressure difference diagram (Inlet flow rate 10g/s)
Chart: Mass flow rate of helium at the inlet （g/s）
| 4 | 6 | 8 | 10 | 12 | 14 | 16
压差Pa | 8.2361 | 16.772 | 28.1237 | 41.8732 | 58.0346 | 76.5527 | 97.2631

## Slide 14
Calculation and simulation
X
Temperature distribution of helium fluid
Inlet flow rate 10g/s, 3.0bar@4.5K
x=3.500 m
x=1.400 m
x=0.060 m
x=1.250 m
x=2.500 m
Helium fluid is heated in the inner channel.
The temperature of the fluid in the inner channel varies greatly near Q1-A
Cooling of quadrupole coils

## Slide 15
Calculation and simulation
X
Temperature distribution inside the inner channel
Temperature distribution on the outer side of the inner channel
Inlet flow rate 10g/s, 3.0bar@4.5K
The temperature of 10g/s subcooled helium increases by about 0.04K, after passing through Q2 and Q1-B.
When subcooled helium flows through Q1-A, its temperature risesrapidly, with a gradually increasing temperature difference at the same X position.
Cooling of quadrupole coils

## Slide 16
Calculation and simulation
Chart: Mass flow rate （g/s）
| 4 | 6 | 8 | 10 | 12 | 14 | 16
Maximum temperature: inside the inner channel | 4.9649 | 4.8373 | 4.7427 | 4.6902 | 4.6637 | 4.6387 | 4.6216
Maximum temperature: Outer side of inner channel | 4.8161 | 4.7071 | 4.6345 | 4.5947 | 4.5741 | 4.5615 | 4.5527
Maximum temperature: inside the outer flow channel | 4.7557 | 4.6667 | 4.632 | 4.602 | 4.5826 | 4.5696 | 4.5602
The static thermal radiation of a quadrupole focusing magnet is constant.
The higher the flow rate, the lower the temperature of the Q1-A magnet.
The flow rate of subcooled helium is determined based on the temperature of the magnet.
Cooling of quadrupole coils

## Slide 17
Possible Improvement
Application cases of large flow forced flow cooling ---- supercritical helium cycle pump:
The electron-proton collider HERA at the electron synchrotron laboratory (DESY) in Hamburg, Germany, uses a 45g/s helium circulating pump. （DESY）
The Atlas-LHC at CERN in Geneva, Switzerland, uses two 600g/s helium circulation pumps and two 1.2Kg/s helium circulation pumps.
The Superconducting magnet Test Facility at the Atomic Energy Research Institute of Japan.
TOSKA at the Institute of Technical Physics at the Karlsruhe Research Center in Germany.
Refrigerator
SC Magnet
LHe
Conventional helium cooling mode
Refrigerator
SC Magnet
LHe
Helium circulation cooling mode
helium circulating pump
Calculation and simulation

## Slide 18
Subcooled LHe Circulation
A tank is used to control the pressure.
The flow rate can be improved largely.
Temperature distribution can be more uniform.
The system is complicated.
Calculation and simulation

## Slide 19
Current leads design
CEPC superconducting inserted quadrupole magnets need to develop 2 kA level current leads;
The traditional pure copper leads are not easy to meet the requirements, and the current feasible solution is to use binary current leads based on high-temperature superconductivity;
The superconducting wire welding resistance optimization, safe protection and low-temperature insulation and other issues are considered;
Current lead in BEPC2
Current lead in KIT

## Slide 20
Supercooled LHe Circulation
Current leads design
HTS current lead
Current leads cooled by liquid nitrogen or helium are designed based on Bi-2223 high-temperature superconductor and high-purity copper;
With the help of numerical simulation, for the cooling of the copper section is designed; An enhanced heat transfer scheme is proposed；
To study the condensation and frosting problems prevalent in current current leads, and explore the inherent frost-free properties of the leads in future;
Research on the design of various cooling sources, such as conduction cooling, low-temperature helium cooling, liquid nitrogen cooling and other methods.
2KA HTS current lead cooled by helium gas
New heat exchanging method
高纯无氧铜
高温超导+分流器
低温超导

## Slide 21: Summary
Design status of cryomodule:
The cryostat has been updated as the optimization of the SC magnets.
Supercritical/ Subcooled liquid helium is used as the cold source.
Double cooling channels of SC magnets can be used, if the mechanical space is allowed.
A subcooled LHe circulation is designed, which can increase the flow rate largely.
Current lead and cryogenic system is designed initially;
Works to be done:
Optimization of the cryostat;
Thermal and mechanical analysis; (quench protection, energy storage , supports )
Current lead design；
Measurement requirements; (temperature/pressure/BPM)
Initial consideration of processing and manufacturing technology;

## Slide 22
EDR plan
EDR plan for MDI SC cryostat:
2024:
Update the design of the cryomodule
Thermal and mechanical analysis of the structure
Optimization of heat and mass transfer of the helium
Design of current leads
2025:
PI＆D scheme determination
Assembly process design and alignment considerations
2026:
Machine-finishing technological design
Cryogenic performance test of critical component

## Slide 23
Thanks for your attention!