## Slide 1
CEPC MDI SC magnet cryostat design and IR region beam pipes
Xiangzhen Zhang, Xiaochen Yang
Cryogenics Group, Accelerator Research Center Institute of High Energy Physics(IHEP)
2024.09.27

## Slide 2: Content
Introduction
Weight optimization of the cryostat
Temperature field of beam pipes
Current leads design for MDI SC magnet
Summary

## Slide 3
  1. Introduction
In CEPC, there are two combined-function Superconducting magnets in MDI
Each combined-function magnet includes double aperture high gradient quadrupole (Q1a, Q1b, Q2) and anti-solenoid, around each side of the IP point.
The cryostat is used to provide the cryogenic environment for SC magnets, which is below 5.0 K.
From Yingshun Zhu
ITEM | Q1a | Q1b | Q2 | Anti-solenoid
Central field gradient (T/m) | 142.3 | 85.4 | 96.7 | 
Cooling type | LHe | LHe | LHe | LHe
Operating current (A) | 780 | 650 | 770 | 1300
Magnetic storage energy (KJ) | 16.7 | 15.2 | 32.1 | 730
Cross section parameter (mm) | Φ40~61 | Φ52~78 | Φ62~88 | 70 sections
Magnet mechanical length (m) | 1.23 | 1.23 | 1.53 | 5.1
Net weight (Kg) | 25 | 32 | 43 | 302
Total weight of magnets (Kg) |  |  |  | 402

## Slide 4
1985mm
1915mm
2885mm
Q1a
Q1b
Q2
Anti-solenoid
Cryostat of SC magnet
The superconducting magnets Q1a,Q1b and Q2 are supported on the inner wall of the solenoid.
The anti-solenoid is supported by a ring on the inner wall of the helium tank.
Vacuum
Thermal shield
LHe tank
Support
Anti-solenoid
Q1a
Beam chamber
  1. Introduction
Notes: 标注尺寸

## Slide 5
2. Weight optimization of the cryostat
Weight: 1184kg
Materials: S304
950mm
1915mm
2885mm
4mm
6mm
472mm
626mm
计算条件 |  | 
压力 | 1 | MPa
温度 t | 300 | K
内径 | 472&626 | mm
负偏差 | 0.3 | mm
腐蚀裕量 | 0.00 | mm
焊接接头系数 | 0.8 | ---
计算条件 |  | 
 | 1 | MPa
温度 t | 300 | K
 | 472&626 | mm
 | 0.3 | mm
 | 0.00 | mm
 | 0.8 | ---
计算厚度：
名义厚度：
有效厚度：- -
根据GB/T 150.3-2011钢制压力容器厚度的计算
Vacuum vessel
Notes: 标注尺寸

## Slide 6
Weight: 195kg
Materials: S316L
2800mm
2300mm
3mm
3mm
298mm
454mm
计算条件 |  | 
压力 | 1 | MPa
温度 t | 4 | K
内径 | 298&454 | mm
负偏差 | 0.3 | mm
腐蚀裕量 | 0.00 | mm
焊接接头系数 | 0.8 | ---
计算条件 |  | 
 | 1 | MPa
温度 t | 4 | K
 | 298&454 | mm
 | 0.3 | mm
 | 0.00 | mm
 | 0.8 | ---
计算厚度：
名义厚度：
有效厚度：- -
根据GB/T 150.3-2011钢制压力容器厚度的计算
2. Weight optimization of the cryostat
Helium tank
Notes: 标注尺寸

## Slide 7
Thermal shield
Weight: 148kg
Materials: Copper
Materials: Aluminum
Weight: 43kg
2. Weight optimization of the cryostat
Notes: 标注尺寸

## Slide 8
Support of SC magnet
Skeleton supports Weight: 142kg
Skeleton supports Weight: 92kg
2. Weight optimization of the cryostat
Notes: 标注尺寸

## Slide 9
Cryostat length: 5.75 m
Total weight: 2.006 ton
Items | Weight (kg) | Main materials
Vacuum vessel | 1184 | SS
Helium Vessel | 195 | SS
Thermal shield and pipes | 43 | Aluminum
SC quadrupoles | 100 | Copper & Aluminum
Anti-solenoids | 302 | Copper & Aluminum
Skeleton supports | 92 | Aluminum
Liquid Helium | 90 | Liquid Helium
Total weight | 2006 | 
2. Weight optimization of the cryostat
SuperKEKB
Notes: 标注尺寸

## Slide 10
3. Temperature field of beam pipes
From Quan Ji and Yudong Liu
右图为高能所刘瑜冬老师提供的热量，单边总热量455.4W；
计算时考虑余量，按单边总热量600W计，即各处热量乘以1.31747；
位置 | 单边总量 | 两边总量 | 面积 | 热流密度
mm | W | W | m2 | W/cm2
0~80 | 72.85 | 145.70 | 0.0100519 | 1.449
80~175 | 38.58 | 77.15 | 0.0119348 | 0.646
175~700 | 488.57 | 977.15 | 0.0843314 | 1.159
全部合计 | 600 | 1200 |  | 
束流管热量加载
IP 附近束流管
Notes: 标注尺寸

## Slide 11
外延铝管：
2个进口，2个出口
冷却介质：水
入口温度：16℃
入口流速：1m/s (3.4L/min)
湍流，下进上出
中心铍管：
4个进口，4个出口
冷却介质：水或1号电火花油
入口温度：16℃
入口流速：0.8m/s (1.1L/min)
层流
换热要求：外铍管温度小于20℃
A
A’
A-A’剖面
铍板
冷却介质 : 水
束流管整体温度分布
最高温度位置
最高温度: 31.1℃
最高温度: 26.7℃
冷却介质: 油
IP 附近束流管
3. Temperature field of beam pipes
Notes: 标注尺寸

## Slide 12
冷却介质 : 油
冷却介质 : 水
外铍管温度云图
外铍管温度云图
Δt=2.4 ℃
ΔP=37.3 kPa
Δt=1.0 ℃
ΔP= 21kPa
连接处
油冷：温度满足要求！
水冷：温度满足要求！
采用水冷效果更好！
3. Temperature field of beam pipes
IP 附近束流管
Notes: 标注尺寸

## Slide 13
上铍板温度
下铍板温度
铍板温度云图
外延铝管截面温度云图(x=585mm)
外延铝管温度云图
3. Temperature field of beam pipes
IP 附近束流管
Notes: 标注尺寸

## Slide 14
热负荷：Synchrotron radiation
Region | ttbar |  | Higgs |  | Z | 
 | SR heat load | SR average power density | SR heat load | SR average power density | SR heat load | SR average power density
0~780mm | 0 | 0 | 0 | 0 | 0 | 0
780mm~805mm | 11.88W | 132W/cm2 | 23.04W | 256W/cm2 | 11.8W | 131.1W/cm2
805mm~855mm | 27.53W | 152.9W/cm2 | 53.39W | 296.6W/cm2 | 27.4W | 152.2W/cm2
855mm~1.9m(Q1a entrance） | 2.22W | 0.59W/cm2 | 4.32W | 1.15W/cm2 | 2.2W | 0.59W/cm2
Q1a（1900-3110）1210 | 1.69W | 0.38Wcm2 | 3.28W | 0.75W/cm2 | 1.68W | 0.38W/cm2
Q1a~Q1b（3110-3190） | 11.8W | 40.97W/cm2 | 22.92W | 79.58W/cm2 | 11.75W | 40.8W/cm2
Q1b（3190-4400） | 2.04W | 0.47W/cm2 | 3.96W | 0.91W/cm2 | 2.03W | 0.47W/cm2
Q1b~Q2(4400-4700) | 36.6W | 33.9W/cm2 | 71.04W | 65.8W/cm2 | 36.4W | 33.7W/cm2
Q2(4700-5900) | 3.74W | 0.69W/cm2 | 7.26W | 1.34W/cm2 | 3.72W | 0.69W/cm2
3. Temperature field of beam pipes
恒温器处束流管
Notes: 标注尺寸

## Slide 15
热负荷：HOM & Resistance wall
Position | Position Start-end（mm） | material | Length (mm) | Higgs(w) & (w/cm2) | W (w) & (w/cm2) | Z(w) & (w/cm2) | ttbar（w） & (w/cm2)
Be pipe (w) | 0-85 | Be | 85 | 1.13 & 0.021 | 5.587 & 0.105 | 55.295 & 1.35 | 0.31 & 0.005
Be pipe transition(w) | 85-180 | Al | 95 | 0.61 & 0.01 | 2.950 & 0.049 | 29.280 & 0.491 | 0.172 & 0.007
Transition pipe (w) | 180-655 | Al | 475 | 6.99 & 0.017 | 34.48 & 0.085 | 341.562 & 0.83 | 1.958 & 0.005
Transition （w） | 655-700 | Al | 45 | 0.62 & 0.015 | 2.95 & 0.071 | 29.28 & 0.701 | 0.172 & 0.004
RVC bellow（w） | 700-780 | Cu | 80 | 0.52 & 0.007 | 2.532 & 0.034 | 25.002 & 0.337 | 0.14 & 0.002
Transition on Y-crotch | 780-805 | Cu | 25 | 0.16 & 0.007 | 0.785 & 0.032 | 7.822 & 0.316 | 0.05 & 0.002
Y- crotch (w) | 805-855 | Cu | 50 | 0.33 & 0.005 | 1.572 & 0.024 | 15.626 & 0.241 | 0.091 & 0.002
Quadrupole pipe(w) | 855-1100 | Cu | 245 | 1.58 & 0.005 | 7.735 & 0.024 | 75.594& 0.24 | 0.434 & 0.002
Total | 0-1100 | - | 1100 | 12.0 &0.011 | 58.594 &0.056 | 580.46 & 0.56 | 3.331 & 0.003
3. Temperature field of beam pipes
恒温器处束流管
Notes: 标注尺寸

## Slide 16
水冷管道
水冷：1.5m/s，2mm*10mm流道；16℃（289K）
256 W/cm2
296.6 W/cm2
1.15 W/cm2
0.75 W/cm2
79.58 W/cm2
0.91 W/cm2
65.8 W/cm2
1.34 W/cm2
辐射光（Higgs）：
作用宽度0.36mm
780mm--
-- 6200mm
计算边界条件
Q1a~Q1b
Q1a
Q1b
Q1b~Q2
Q2
3. Temperature field of beam pipes
入口
出口
恒温器处束流管
Notes: 标注尺寸

## Slide 17
真空盒温度
780-805mm；
805-855mm
Q1a~ Q1b ；
Q1b~ Q2；
Thermal 校核计算（315K）
温度云图
3. Temperature field of beam pipes
恒温器处束流管
Notes: 标注尺寸

## Slide 18
水冷速度场
中心水流速度在2.1m/s
压差损失1.5bar
冷却水速度场
冷却水截面速度
3. Temperature field of beam pipes
恒温器处束流管
Notes: 标注尺寸

## Slide 19
沿程的温度场分布，几个位置温度升高较明显；真空盒温度，最高313K（40℃），冷却水温度，最高293K，出口291K。
水冷：温度满足要求.
温升~1.5℃.
780-805mm；
805-855mm
Q1a~ Q1b ；
Q1b~ Q2；
真空盒温度
冷却水温度
3. Temperature field of beam pipes
恒温器处束流管
Notes: 标注尺寸

## Slide 20
4. Current lead design for MDI SC magnet
MDI superconducting anti-solenoid magnet need to develop 1.3 kA level current leads;
The traditional pure copper leads are not easy to meet the requirements, and the current feasible solution is to use binary current leads based on high-temperature superconductivity;
The superconducting wire welding resistance optimization, safe protection and low-temperature insulation and other issues are considered;
Current lead in BEPC2
Current lead in KIT
Notes: 标注尺寸

## Slide 21
HTS current lead
Current leads cooled by liquid nitrogen or helium are designed based on Bi-2223 high-temperature superconductor and high-purity copper;
With the help of numerical simulation, for the cooling of the copper section is designed; An enhanced heat transfer scheme is proposed；
2KA HTS current lead cooled by helium gas
New heat exchange method
高纯无氧铜
高温超导+分流器
低温超导
 | 1300A电流引线 |  | 800A电流引线 | 
引线段 | HTS | 铜引线 | HTS | 铜引线
冷却 | 5K氦气迫流 | 5K氦气迫流 | 5K氦气迫流 | 5K氦气迫流
结构 | Bi-2223银金高温超导带 | RRR40的高纯无氧铜 | Bi-2223银金高温超导带 | RRR40的高纯无氧铜
长度mm | 390 | 619 | 390 | 619
截面 | 12层 | 直径20mm，翅高5mm | 6层 | 直径20mm，翅高5mm
工作温区 | ＜60K | ＜60K-300K | ＜60K | ＜60K-300K
载流A | 1500+ | / | 900+ | /
低温漏热 | ＜0.15 | / | ＜0.1 | /
氦气g/s | / | 预估＜0.1 | / | 预估＜0.05
4. Current lead design for MDI SC magnet
Notes: 标注尺寸

## Slide 22
计算得到铜的温度场，在0.06g/s氦气流量下，可满足要求。工艺更简单，流量可更小，绝缘更容易实现。
序号 | 项目 | 描述
1 | 载流能力 | 77K最大1800A @AS1，900A @SCQ。
2 | 铜段加工 | 翅片铜柱，工艺简单可靠，并大幅缩短制作周期。
3 | HTS | 有效提高铜段低温端温度，极低漏热，使得低温超导处的温度容易控制。
4 | 电绝缘 | 室温陶瓷，沿程G10套管，综合耐压可达1000V+。
5 | 低温漏热 | 大幅减小，小于一元引线情况的1/10。
二元电流引线的技术特点：
4. Current lead design for MDI SC magnet
Notes: 标注尺寸

## Slide 23: Summary
Design status of cryomodule:
The cryostat weight has been optimized to be approximately 2.0 tons.
The temperature field of the beam pipe has been calculated and checked, which meets the requirement.
Binary current leads have been designed initially for the SC magnets.
Works to be done:
Optimization of the cryostat and cooling system.
Thermal and mechanical analysis; (quench protection, energy storage , supports )
Measurement requirements; (temperature/pressure/BPM)
Initial consideration of processing and manufacturing technology;

## Slide 24
Thanks for your attention!