## Slide 1: Cryogenics : How to Achieve Low Temperature and Production of Cryogen : Process Cycle/ Thermodynamics
T S Datta (Retired From )
Indian Institute of Technology. Kharagpur. India
&
Inter University Accelerator Centre. Delhi

## Slide 2
Outline of my Lectures
Introduction on Cryogenics
How to Produce Cryogen
    Thermodynamic Process ( Carnot )
    Liquefaction Cycle
    Performance of Cycle
Practical Helium Liquefier/ Refrigerator
    How far from theoretical Cycle
    Components
4. Properties of Material at Cryogenic Temperature
( If Time Permits ): Most Probably No

## Slide 3
Sun
6000K
SO2 -liquid
Ice
Room Temp
Water Boils
NH3- liquid
373K
300K
263K
273K
240K
4.2K
111K
90K
77K
20K
LN2 -liquid Nitrogen
LOX -liquid Oxygen
CH4 –liquid ( LNG)
LH2 -liquid Hydrogen
LHe -liquid Helium
0 K - Absolute Zero
Cryogenic
Temperature
range
120K
Cryogenics
boundary
Temperature Scale
Why?
Superfluid Helium
2.1K
Lowest Temp:
500 pico K

## Slide 4
Cryogenics
DIRECT
Indirect Through Superconductivity
LNG
Gas Separation
Preservation ( Food, Blood, Stem Cell), Cryo Surgery
Space
Cryo Pump
Power Application ( Cable, Motor, SFCL)
Cooling of IR Detector,
MRI / NMR
Particle Accelerator
80 K
20 K
4.2 K

## Slide 5
CRYOGEN STORAGE VESSEL
Small container 10- 60 L
100- 500L Pressurized
20,000 L Storage Vessel
at IUAC
Transport Vessel

## Slide 6
Property | He | N2 | Water
Boiling Point | 4.2K | 78K | 373K
Density | 0.12kg/liter | 0.81kg/liter | 1kg/litre
Heat of Vaporisation | 20KJ/ kg | 198 | 2250
Liquid evaporated on 100 W Heat input | 140 L/ hr | 2.2 L/hr | 0.16 L/hr
WHY STORAGE IS SO CRITICAL ?
A. LOW LATENT HEAT ( L)
B. LARGE TEMPERATURE DIFFERENCE ( Tr- Tb)
1 W HEAT LOAD EVAPORATES 34 LITRES LHe / DAY
THANKS TO MLI ( MULTILAYER INSULATION TECHNOGY)
EVAPORATION RATE ONLY 1 LITRES/day in 100 Litres Vessel

## Slide 7
Earlier Laboratory techniques for reducing temperatures and Liquefaction
Liquefaction of gas at high pressure in a thick-walled glass tube surrounded by ice ( 273 K),
A rapid expansion of the vapor phase to atmospheric pressure through a valve.
The temperature of the remaining liquid phase then dropped to its NBP.
a) Isothermal Compression
b) Rapid Expansion
ICE
Liquid at High Pressure
Liquid at NBP
Ethylene, could be liquefied with a critical temperature of 282 K and a normal boiling point temperature of 169 K,
Methane, Nitrogen, hydrogen, Helium that could not be liquefied by this technique, even with pressures up to 40 MPa, were called “permanent”gases.
PERMENANT GASES
LPG

## Slide 8
T(boil)
T(critical)
P(critical)
SO2 263K 432K 79 Bar
NH3 240K 405K 115 Bar
H2 ( LH2) 20K 33K 13Bar
N2 (LN2) 78K 126K 34Bar
O2(LOX) 90K 155K 50 Bar
He(LHe) 4.2K 5.2K 2.2 Bar
Permanent Gases
Tc [SO2/NH3] > 273K ( ICE temp)
gas
liquid
Pressure
Tc [N2/He] < 273 K (ICE Temp)
gas
Whatever Pressure ?
No liquid
Hence they are called
Permanent Gases
Ar, N2, O2, Air, Ne, H2 and He
LNG
&
LPG ??
CH4 112 191K 46 Bar
C2H4 169 282 50
CRYOGENIC RANGE

## Slide 9
1852
1898
James Dewar
Wroblewski and Olszewski
L. Cailletet
Pictet
P. Kapitsa
JT Effect Discovered
1877- 1883
Oxygen / Nitrogen Liquefied
Hydrogen Liquefied
1902
Expansion Engine for Air
July 10, 2008
Helium Liquefaction
James Joule
W. Thomson
1934
Helium Liquefaction with Claude Cycle
HISTORY ON LIQUEFACTION OF PERMANENT GASES

## Slide 10
DOMESTIC REFRIGERATOR
We can not use similar principle for Cryogenic Refrigerator, because Critical Temperature of Cryogenic gases are much below Room Temperature

## Slide 12
REFRIGERATOR & HEAT ENGINE
Th
TC
Qh
QC
W =Qh-QC
2nd Law of Thermodynamics: It is not possible for heat to flow from a colder body to a warmer body without any input of Work
Second Law of Thermodynamics: It is impossible to extract an amount of heat QH from a hot reservoir and use it all to do work W .
W
QC
Qh= QC+W
TC
Th
COP R,Carnot =Qc/ W
= TC/( Th- TC)

## Slide 13: Power ( W) required to extract 1 W refrigeration at Tc is : 1/ ( COP) =
TC=200 K , W = 0.5 W
LN2 : Tc = 78 K , W = 1.68 W
LHe : Tc = 4.2 K, W = 70 W
Tc= 2 K , W = 150 W
Tc = 0.01 W= 30k W
These are Theoretical minimum Power. We have to multiply first with efficiency of the Cycle and then multiply with mechanical efficiency of all Components ( Compressor, Heat Exchanger, Expander of refrigerator)
Actual work = Wc/( ηCycle * ηComp)
Required Plug Power for 1 W refrigeration at 4. 2 K = 500- 225 W
Total efficiency may be 10 to 30 % at 4.2 K
Required Plug Power for 1 W refrigeration at 2K = 1000- 1500 W
Th = 300 K Tc vary from 200 K to .000001 K

## Slide 14: BASIC THERMODYNAMIC PROCESS FOR COOLING
A. ISOTHERMAL COMPRESSION ( Compressor)
B. ADIABATIC EXPANSION ( Turbine)
C. ISENTHALPIC EXPANSION ( JT VALVE)
D. ISOBARIC COOLING ( Heat Exchanger, Precooler)
P1, V1,T1
P2,V2, T1
Process A
Process B
T3 < T1 ( Cooling)
Isothermal compression is achieved with water/ air cooling System. W = m. T ( R/ M) ln ( P2/P1) . Example : 1 gm/s gas T= 300 K, P2/ P1 = 15
Helium : 1600 W ( 20 NM3), N2 = 200 W (2. 8 NM3 )
P1, V1, T3
Insulation
dQ=0

## Slide 15
For Process Cycle Evaluation we use the following Thermodynamic Parameters
Fundamental :
Pressure ( P)
Temperature ( T)
Volume ( V)
Gas Constant (R)
Work ( W)
Heat ( Q)
Internal Energy ( U)
Entropy ( S)
Enthalpy ( H )
W
Q
m1( p1,T1)
m2( p2,T2)
m3( p3,T3)
h1
h2
h3
Energy & Mass Balance
AND
P1, V1,T1
dQ
dW
P1, V2,T2
Try to understand difference of Cp and Cv . Home work ?

## Slide 16
SAMPLE TEMPERATURE- ENTROPY CHART FOR NITROGEN
Constant Enthalpy Curve
Constant Pressure Line
Liquid Vapour Inter-phase
1
2
3
4
5
1( 1bar, 280 K)-2 (100, 280) : Isothermal Compression
2(100,280)-3(100,150) : Isobaric Cooling ( HX)
3(100,150) -4( 1,78) : Isenthalpic Cooling ( JT)
5(1,78) -1(1,280) : Isobaric Heating ( HX)
2a
2 (100, 280)-2a ( 10-155):
Adiabatic Expansion/
Isentropic Cooling
Critical Temp

## Slide 17: LIQUEFACTION OF PERMANENT GASES
Qr = Sensible Heat + Heat of Vaporization
GAS AT 300 K
LIQUID AT NBP
Qr
Work
(Qr) = Nitrogen 234 J/ gm ( 300K to 78 K ) + 199 J/gm
Helium : 1542 J/ gm ( 300 K to 4.2 K) + 20 J/ gm
Sensible Heat
Latent Heat

## Slide 18
To Liquefy Permanent Gases
Cooling
Isenthalpic
(JT)
Isentropic
By JT Valve
( No External Work)
By Expansion Engine/Turbine
( Do External Work)
Indirectly By Other Cold Liquid/ Gas
( Heat Exchanger
Cooling co- efficient
μ should be positive
Higher is Better
High Pressure to Low pressure

## Slide 19
Isenthalpic /JT Cooling
For an Ideal Gas
Fortunately Gas does not behave ideally
Real Gas : Vander Wall
For an Ideal Gas

## Slide 20
When , 2a/RT > b,
0r T < 2a/bR
μjT is Positive , Hence Cooling
When , 2a/RT < b,
μjT is Negative , Hence Heating
At large specific volumes
Inversion curve is represented
by all points , where μjT =0
Maximum Inversion Temperature
Timax = 2a/bR ( at p=0 or b/v=0)
Isenthalpic /JT Cooling
b

## Slide 21
Gas | He | H2 | Ne | N2 | Ar | O2
Timax (K) | 45 | 205 | 250 | 621 | 794 | 761
Above Max inversion temperature ( Timax )we will not be able to cool the gas for any set of pressure combination.
Just below their max inversion temperature drop in temperature is not significant and temperature drop increases as we lower the inlet temperature and max above their critical temperature.
That's the reason JT is always incorporated in the last stage of liquefaction cycle. It can also handles liquid gas mixture unlike turbine
Above RT
Temp Drop More
Temp Drop Less

## Slide 22
Pdv=0 , dh=0 and
Hence du=0
Difference ( KE+ PE) = 0
Pressure
Expansion from A to B :
Potential Energy increases and hence KE decreases ( Temp Drop)
Expansion from C to D :
Potential Energy decreases and KE increases , Temp increases
JT COOLING/ HEATING
The internal Energy is the sum of thermal kinetic energy and thermal potential energy. Thus, even if the internal energy does not change, the temperature can change due to conversion between kinetic and potential energy;

## Slide 23
Adiabatic Expansion ( Isentropic Cooling)
P1, V1, T3
Insulation
dQ=0
dS=0 ( Isentropic)
High Pr
Low Pr
High Pressure Gas does an External work (Lifting Piston) and comes out at low Pressure and low temperature
Unlike JT Expansion, There will be always cooling effect on adiabatic expansion at any temperature and Pressure
Temperature drop is much higher compared to JT Expansion
Always Positive
( Only Cooling )

## Slide 24
Comparison of Cooling Effect by JT & Isentropic Expansion
Through T- S Chart
Isentropic
1
2
3
1 (19k, 10 bar) - 2 ( 17 K, 1 Bar) : JT Cooling
Drop only 2 K
1 (19k, 10 bar) - 3 ( 7 K, 1 Bar) :
Isentropic Cooling
Drop 12 K
(dT)s >>(dT)h
Isenthalpic

## Slide 25
Adiabatic ( Isentropic) Expansion
= 1.66 ( He, Monatomic Gas)
=1.4 ( N2, Diatomic Gas)
Example : If Helium Gas is Expanded from 220 Psi ( p1) to 18 Psi ( p2) at
Inlet temperature ( T1) = 60 K
T2 = 23.4 K , Actual Case it is 30K
Efficiency = 80 %

## Slide 26
LIQUEFACTION SYSTEM PARAMETERS
Work Required per unit mass liquefied = W/mf
Yield ( What fraction of Compressed Gas is liquefied) , y= mf/m
Ideal work required per unit mass liquefied= Wi/mf
Figure of Merit : Ideal work/ Actual work for the cycle
FOM= (Wi/mf)/ (W/mf) : 0 to 1

## Slide 27
Ideal Thermodynamic Liquefaction Cycle
1----2 : Isothermal Compression
2----f : Isentropic Expansion
Not Possible , Why ???
For N2, if P 1 is I bar, then P2 must be 700000 Bar ( very high pressure) to liquefy all the gases
Liquid Yield ( Y) = mf/m= 1
Not Practical
Ideal Work Requirement for 1 Kg Liquid Production
N2 = 768 KJ, He = 6800 KJ,

## Slide 28
Primary Practical Nitrogen Liquefier ( Linde- Hampson Cycle)
1-2,Isothermal Compression
2-3 ,Isobaric Cooling
3-4 Isenthalpic Cooling
It is only for those gases ( N2, O2, Ar) whose
Timax is above RT
<<1
Yield can be increased by Increasing Pressure ( lower h2), Other parameters are fixed but at what cost ??
We need Compressor / High Pressure Gas cylinder , Heat Exchanger & JT to Produce LN2

## Slide 29
A simple table on liquid yield and work required per unit production of liquid nitrogen for various compressor discharge pressure is presented here
( T1 = 300 K, P1 = 1 bar absolute pressure, h f = 30 J /gm. h1 = 462 J/ gm )
Pressure (P2 ) | h2 | Y=mf /m | W/mf | FOM
20 bar | 454 | 0.02 | 12888 | 0.06
50 | 448 | 0.03 | 9937 | 0.08
100 | 438 | 0.06 | 7200 | 0.11
200 | 425 | 0.09 | 5564 | 0.13
FOM = Ideal Work Required/ Actual Work
We Need Very High Pressure to have Significant Percentage of Liquid Production on this L- H Cycle

## Slide 30
For 10 liter/ hr (8 kg/hr) liquid nitrogen production : Compressor capacity required at 100 bar discharge pressure
m= mf x y = 8 kg/hr/0.06 = 133 kg/hr = 106 M3/hr
Theoretical Power : 7200 kJ/kg x 8/ 3600 = 16 kW ?
Pressure | Yield mf/m | W/mf ( J/ Kg)
100 Bar | 0.06 | 7200
Considering the efficiency of Compressor and Heat Exchanger, the Actual power Requirement will be more than Double 40 kW
Power Cost of Liquid nitrogen will be Rs 20/ Litre
Actual Power cost is only Rs 5/ litre
This Cycle is Simple but not Cost Effective
Analysis on Linde- Hampson Cycle
Can we use the same Cycle for Helium Liquefaction ?? No
You can calculate the cost of Liquid nitrogen based on your own parameter

## Slide 31
Yield
Effectiveness of Hx
0.8
1.0
0.08
0.0
0.87
Example : p1= 1 bar ,p2= 200 bar, N2, 300 K
Heat Exchanger Efficiency on Linde Cycle
If Efficiency less than 0.87 , Production will be zero

## Slide 32
Yield is higher, Hence W/ mf will be less
3

## Slide 33
LIQUID YIELD for Nitrogen CAN BE INCREASED BY PRECOOLING
( by lowering the value h1)

## Slide 34
Max Inversion Temperature for Helium : 45 K ( Below RT)
Basic Linde- Hampson system will have Heating Effect.
We have to Precool with Liquid Nitrogen ( 78 k) and Liquid Hydrogen ( 20 K) prior to JT .
( First Liquefaction of Helium in 1908 : By Precooling L- H)
ALTERNATIVELY : ADDING ONE ADIABATIC EXPANSION PROCESS BY USING A TURBINE : Next
LIQUEFACTION OF HELIUM
15 K
9 K
LH2
LN2
PUMP
100 bar
80 K
First Helium Liquefier
By Kamerlingh Onnes

## Slide 35
CLAUDE CYCLE

## Slide 36
e’
m
m
m-me
me
m-me-mf
m-mf
mf
mf
Optimized value with
Single Expander
X~ 60 to 80 %
Higher flow rate through the Expander will have higher cooling, that reduces the temperature (5). More fraction of liquid
Remember, Mass flow rate through JT is also reducing

## Slide 37
Assumptions
Compressor and Expander Efficiency is 100%
Heat Exchanger Effectiveness is 1
Pressure drop is negligible
Heat Transfer to the Cold system from the Surrounding is Zero
We will consider the effect of efficiency on cycle performance in later stage

## Slide 38
Popular During 1950-80

## Slide 39
Here Yield can be optimized with
T3, T5, x1 and x2 at
different pressure ( p2)
For standard Helium Liquefier T3= 60 K, T5 = 20 K
X1= 15 %, x2 = 40 %

## Slide 40
Capacity can be further enhanced by using two Expander and precooled with liquid Nitrogen. This is called Modified Claude Cucle.
HELIUM LIQUEFIER WITH TURBINE
Advantage : Turbines are more reliable than the expansion engines because the latter are susceptible to performance deterioration due to contamination.
Disadvantage : Turbines do having a limited expansion ratio, that is a limited ratio of inlet to outlet pressures.
That was the reason Turbine are used in series rather than parallel for Reciprocating Expander
Standard 1 kW class Refrigerator
Initial year, isentropic expansion was achieved by Reciprocating Piston type and later Turbine
300 litres/hr

## Slide 41
Major Components :
Compressor
Heat Exchanger
Expander
JT Valve
Commercial Helium Liquefier with Temperature at Different Process Point

## Slide 42
Most Popular Helium Liquefier in Low Temperature Laboratories ( 1965 – 1980)
Capacity : 10 litre/hr ( single Compressor) : Reciprocating 2 stage; 100 NM3/hr , Reciprocating Expansion Yield = .08
ADL to CTI 1400
CTI 1410 KOCH PSI LINDE ( L 1410)
Automatic Engine speed, Screw Compressor, Modular
Production rate : 10 litres/ hr to 50 litres/ hr

## Slide 43
18 kW at 4.5 K Helium Refrigerator for CERN LHC Project
LINDE
AIR Liquide
Largest helium refrigerator with Single Cold Box
Next 20 / 25kW ??

## Slide 44
Strobridge Survey (Efficiency) 1974
GM Cryocooler ; 4 kW for 1W refrigeration at 4.2 K
Laboratory Scale Helium Refrigerator ( ~ 100 W) : 700 W for 1 W
Medium Range 1kW Class ( 300 W for 1W Range)
Large Helium Refrigerator ( 18 kW for CERN : 225 W for 1 W
Whether we have reached peak value of 225 W ??

## Slide 45
STANDARD HELIUM LIQUEFIER/ REFRIGERATOR CYCLE
Standard 1 kW at 4.3 K Helium Refrigerator needs a Compressor with capacity 100g/s and discharge pressure at 13 bar (g)
Isothermal Operation : Work required
Actual Plug Power ; 305 kW
Compressor Efficiency : 49%
Inverse COP = 300 W/ W

## Slide 46
Major Components of Helium Refrigerator
Turbine
Heat Exchanger
Oil Removal System

## Slide 47
Helium Refrigerator Layout @CERN
18 kW Refrigerator
LHe Distribution Line
Beam Line
Compressor Station
Cold Box

## Slide 48
Liquefaction Vs. Refrigeration ?? I Important
Same Thermo dynamical Cycle as Liquefaction Cycle. Difference in way of operation
HOW?
300K
4.2K
Cold Box
LHe
Load
Cold Box
L
O
A
D
Load may be the
S.C. magnets
& Cavities
Cold
vapour
Cold
vapour
warm
gas
Refrigerator Mode
Liquefaction Mode
Warm Gas

## Slide 49
Liquefier 100 L/hr = 3.33 g/sec = 3.33 x 20 j/g = 66.6 W
But we can get << 300W on Running as Refrigerator
Thumb Rule: 1L/hr ~ 3-4 W
Why ???
Cold Enthalpy 4.2- 300 K is used
JT Temp will be lower and hence yield
Liquefaction Vs. Refrigeration

## Slide 50
Thanks
Contact mail : tsdatta59@gmail.com
Namaste
Next : Let’s move to the real world of Cryogenics through Lectures from Prof. Zhengrong Ouyang, Prof. Hirotaka Nakai , Prof. Xilong Wang and Prof. Ge Rui
What is my and Yours Carnot Efficiency ???
See you on Sunday ( @ Beautiful Great Wall of China)