## Slide 1: Installation of the Veto 100t/h water system and the detector filling
Cong Guo
On behalf of JUNO collaboration
2025-07-22

## Slide 2
Outline
Motivation
  Why does JUNO need a 100 t/h ultrapure water system?
System requirements
  What performance metrics does the system need to meet?
System composition
  How was the 100 t/h water system designed and installed?
System performance
  What are the working conditions of the 100 t/h water system during water filling?
  How does the system perform during circulation mode?
Summary

## Slide 3
Motivation
The Central Detector (CD) is submerged in a Water Cherenkov Detector (WCD), which consists of 40 ktons of Ultra-Pure Water (UPW) and 2400 MCP-PMTs;
For safety and background, the CD was filled with UPW simultaneously with the WCD in the initial filling, 65 ktons of UPW will be used totally ;
CD
WCD
LS
UPW

## Slide 4
Motivation
Water in the WCD:
  Keep the temperature within 21 ± 1℃ for CD stability；
  Keep the attenuation length larger than 40 m for high WCD muon detection efficiency;
  Keep the radon concentration less than 10 mBq/m3 to reduce single rate contribution to CD;
Water in the CD:
  Avoid permanent effects on the LS background;
    Keep particle number meeting JUNO-50 standard (1660 counts/L);
    Keep the radium concentration less than 50 μBq/m3;

## Slide 5
System requirements
The UPW system should have 100 t/h water production and circulation ability;
In the output water of the 100 t/h water system:
  The water quality should be good:
    Resistivity ≥ 18 MΩ*cm ；
    Oxygen concentration < 50 ppb;
  The temperature should be adjusted from 15-22 ℃；
  The particle number <1660 counts/L (JUNO-50 standard);
  The radon concentration <10 mBq/m3;
  The radium concentration <50 μBq/m3；
  The 238U/232Th concentration <10-15g/g;

## Slide 6
System Composition
The water system uses tap water as the source water and passes through 30+ devices to produce UPW.
Water room on the ground
Water room underground

## Slide 7
System Composition
Temperature adjustment:
  3 stages of Exchanger;
Gas removal (Radon/Oxygen):
  Microbubble device + 5 stages of Degassing membrane;
Ion removal (Radium)：
  Radium removal resin + 2 stages of RO + EDI + Polishing resin + Ultra-Filter
Particle removal：
  5 μm filter bags + 5 μm filter cartridge + 0.1 μm filter cartridge + 2 stages of RO + Ultra-Filter

## Slide 8
System Composition
Water pipes, valves, filters, and electronic control cabinet installed in the overground water room.

## Slide 9
System Composition
Water tanks, RO membranes, EDI modules, and microbubble devices installed in the underground water room.
Water tank
RO
EDI
Microbubble

## Slide 10
System Composition
Water inlet
One pipelines to CD:
  Supplied UPW to CD in initial filling;
  Pump UPW out from CD in LS filling;
Six pipelines to WCD:
  One to the water inlet located at the corner, supplying UPW during initial WCD filling;
  Four to the water distributors located at the top and bottom of the CD, supplying UPW during water circulation;
  One to the water distributor located near the equator, pumping UPW out from the WCD.

## Slide 11
System Composition
Water pipelines, water distributors installed in the water pool;

## Slide 12
System performance — UPW filling
On Dec 18th, 2024, UPW filling for CD and WCD started.
On Feb 1st, 2025, UPW filling completed, 40 ktons of UPW was filled in the WCD, and 25 ktons of UPW was filled in the CD.

## Slide 13
System performance — UPW filling
To maintain the stability of the acrylic sphere, water levels in CD and WCD were well controlled, and UPW was simultaneously filled into the CD and WCD.
Water flow rate in CD varied from 0 to 50 t/h, and that in WP varied from 20 to 90 t/h;
Filling flux [m3/h]
WP
CD

## Slide 14
The temperature of the water sending to CD and WCD can be controlled separately;
Water sending to CD will be in direct contact with the acrylic;
Water sending to WCD through the water inlet near the WP wall;
Water in the pool needed to counteract the heat generated by the electronics and dissipated by the pool walls.
The temperature for CD stabilizes at 18.5 ~19.0 ℃, while for WCD, it changes from 15 ~ 20 ℃.
01-27
12-18
01-17
01-07
12-28
Water entering CD
System performance — UPW filling

## Slide 15
01-27
12-18
01-17
01-07
12-28
Oxygen concentration
Water quality was good during filling, the resistivity and oxygen concentration in water were measured online:
  The resistivity of the produced water has been maintained at 18.2 MΩ*cm;
  The oxygen concentration in the water was ~10 ppb at the beginning of filling, and then it was continuously reduced through the optimization of the system, and finally stabilized between 1-2 ppb.
System performance — UPW filling

## Slide 16
The particle numbers in the water was measured using a commercial instrument, the bettersize C400.
The sample volume for each measurement is 20 mL;
The particle number is between 50~350 counts/L, meeting the JUNO-50 standards (1660 counts/L);
Device changed afterwards
System performance — UPW filling

## Slide 17
The radon concentration in water is measured with a self-developed system, which consists of:
  Atomizer: transfers radon from water into gas;
  Dehumidifier: reduces the humidity of the gas for radon detection;
  Radon detector: determines the radon concentration based on the electro-collection.
The sensitivity for this system is 0.42 mBq/m3, details can be found in NIM A 1063 (2024) 169244;
System performance — UPW filling

## Slide 18
A microbubble device and five stages of degassing membranes are used to remove radon from water;
The degassing efficiency decreases as the gas concentration in water decreases;
Microbubble device can generate bubbles in the size of nm~μm, thus increase the gas concentration in water;
The combined application of microbubbles and degassing membranes reduced the radon concentration in water from 10 Bq/m³ to ~5 mBq/m³; realized >99.9% radon removal for single pass.
01-27
12-18
01-17
01-07
12-28
Radon concentration
System performance — UPW filling

## Slide 19
Mn-fiber
The Radium concentration in water is determined with a self-developed system, which consists of:
  Low-background Mn-fiber, which is used to extract radium from water;
  Extraction column, in which water flows through;
  Emanation chamber, in which radium decays and produces radon;
  Radon emanation measurement system, which is used to determine the radium concentration;
The sensitivity of this system is 6 μBq/m3, details can be found in NIM A 1063 (2024) 169257;
System performance — UPW filling

## Slide 20
The 238U/232Th concentration in water is measured by a commercial ICP-MS;
Device sensitivity for UPW measurement:
  ~0.1 ppq (10-17g/g) for 238U;
  ~0.4 ppq for 232Th;
Measurement results:
  0.4 ± 0.1ppq for 238U;
  <0.4 ppq for 232Th;
System performance — UPW filling

## Slide 21
Milestones of the UPW system
Company bidding
Equipment sent to onsite
Underground
system installation
Circulation
started
May, 2019
Apr, 2022
Nov, 2024
Feb 2nd, 2025
Dec 18th, 2024
UPW filling
started
Dec, 2023
Overground
system installation

## Slide 22
The water system has been transferred to WP circulation since 2nd Feb. After 2 volumes of circulation, the output water of the WP:
  The resistivity increased from 1.1 MΩ*cm to 4.8 MΩ*cm;
  The particle number in the water reduced from ~20000 counts/20mL to ~1000 counts/20mL;
02-02
02-12
02-22
03-04
03-14
03-24
Resistivity of the WP output water
Water inlet changed from bottom to top
System performance — WP circulation
Particle number in the WP output water

## Slide 23
02-02
02-12
02-22
03-04
03-14
Radon concentration in the WP output water
System performance — WP circulation
With 2 volumes of circulation:
  The radon concentration reduced from 180 mBq/m3 to 9.5 mBq/m3, which is mainly due to the radon decay;
  The radium concentration reduced from 5 mBq/m3 to 1 mBq/m3 ;
  The 238U concentration reduced from 229 ppq to 62 ppq;
  The 232Th concentration reduced from 23.8 ppq to 8.8 ppq;
The radon concentration in the water system output water was <1mBq/m3, which is mainly due to the radon reduction in the source water of the system.

## Slide 24
Water circulation started
System performance — WP circulation
The water attenuation length is measured by an online system located at the bottom of the WP;
Attenuation length increased from ~23 m to 61.7 ± 3.1 m.

## Slide 25
Summary
A 100 t/h UPW production and circulation system is built to supply UPW for WCD and CD;
In the production mode, the quality of water fully met the requirements for JUNO filling;
In circulation mode, it continuously improved the water quality in the WP.
The 100 t/h water system will be running for 30 years along with the JUNO experiment.