## Slide 1: The Fast Protection System for CSNS-II
The MicroTCA/ATCA International Workshop For Large Scientific Facility Control
Sep.15-Sep.17, 2025, Chongqing, China
Peng Zhu

## Slide 2
Outline
Overview of FPS for CSNS
Current status
Design and development for CSNS-II
Summary

## Slide 3
SC Linac 300 MeV
25 Hz @ ~600 μs
Overview of the CSNS Linac
Phase I: 80MeV, running now
Phase II: 300MeV, preparation stage.20 Spoke & 28 Ellip Cavities
The fourth pulsed spallation neutron source worldwide
National acceptance on August 23, 2018
Operating efficiently and stably for seven years
Update approved in 2024, total about six years

## Slide 4
High availability, high reliability, and high efficiency, ensuring the long-term stable and safe operation.
Objectives：
Objectives and Performance
Must be controlled within 8 μs, including fiber-optic transmission delay, intrinsic device delay, and interlock signal debouncing.
Metrics ：

## Slide 5
Outline
Overview of FPS for CSNS
Current status
Design and development for CSNS-II
Summary

## Slide 6
Interface between FPS and equipment systems |  | 
 | Device | Quantity
Input | MPS | 4
 | TM | 1
 | RMS | 1
 | LLRF | 8
 | PS | 120
 | BLM | 176
Output | IS | 1
 | Chopper | 1
 | RFQ | 1
 | LLRF | 8
access station
layout of interlock chain
Architecture: VME-based on the access layer, aggregation layer, and execution layer
Current Status for CSNS
aggregation station
execution station

## Slide 7
the high-speed transmission link based on 2.5 Gbps
Advantage: Fully hardware-based architecture to minimize signal transmission delay
the custom backplane and the point-to-point transmission
Intra-Site:
Inter-Site:
Current Status for CSNS
the main logic board
“OC”for sharing logic
Point-to-point transmission via custom backplane bus in chassis
High-speed transmission using rocket I/O

## Slide 8
large-scale scientific facility (Linac) | response time
SNS | ≈ 8.0 μs
J-PARC | ≈ 7.5 μs
CSNS | ≈ 2.2 μs
 | total time from receiving the fault signal to cut off the timing for ion source | total time from receiving the fault signal to cut off RFQ Power
Results | ≈ 2.2 μs | ≈ 1.4 μs
Current Status for CSNS
Performance: The response time for Linac

## Slide 9
Outline
Overview of FPS for CSNS
Current status
Design and development for CSNS-II
Summary

## Slide 10
Signal link : Between each substation and the executing station
Each Rocket IO channel processes 16 signals, and the maximum number of signals that the master station can handle：≈1800（14*100 + 14*7*4）
14*7*4
Each substation independently connects to 100 interlocking signals.
ILK
RMS
RST
RST
TM
Timing
DC-DC Power Supply
(DTL #1)
MPS
ILK
DC-DC Power Supply
(DTL #2)
DC-DC Power Supply
(MEBT / SC #1)
DC-DC Power Supply
(MEBT / SC #2)
Linac
RF LLRF
Linac
BLM #1
Linac
BLM #2
executing
station
RTBT BLM #2
aggregating
substation
R4 BLM
RTBT BLM #1
R3 BLM
R2 BLM
R1 BLM
LTBT BLM
Beamline BLM
TM
Timing
interlock logic output
New architecture for CSNS-II

## Slide 11
Total time from beam loss to chopper timing shutdown.：≈ 4 μs
Total time from beam loss to RFQ power reduction：≈ 3.6 μs
Total time from beam loss to shutdown timing of the ion source extraction power supply.：≈ 4.5 μs
Response time estimation in Linac(including fiber-optic transmission delay)
MEBT
RFQ
IS
DTL
LRBT
L
-
DUMP
LRDMP1
Elliptical
cavities
Double
-
Spoke
cavities
ILK
RMS
RST
RST
TM
Timing
DC-DC Power Supply
(DTL #1)
MPS
ILK
DC-DC Power Supply
(DTL #1)
DC-DC Power Supply
(MEBT / SC #1）
DC-DC Power Supply
(MEBT / SC #1）
B
Linac
RF LLRF
Linac
BLM #1
Linac
BLM #2
executing
station
aggregating
substation
TM
Timing
Chopper
~ 1.2
μ
s
~ 500 ns
~ 800 ns
~ 800 ns
~ 800 ns
~ 250 ns
250 ns ~ 1000 ns
New architecture for CSNS-II
BLM

## Slide 12
MEBT
RFQ
H-
DTL
LRBT
Double-Spoke cavities
Elliptical cavities
Benefit: Provide real-time beam loss data with high-precision timestamps for beam commissioning and machine studies
Integrate beam loss and FPS
Challenges：
Ultra-high reliability
Ultra-high accuracy
High-precision timestamps(EVR)
Integrity and immunity
… …
parameter acquisition
Real-Data acquisition

## Slide 13
Tendency: (1) VME --> xTCA,
Considerations for Hardware
(2) demo FPGA --> RAM + Linux + EPICS (Embedded IOC),
(3) distributed data --> Associated data with high-precision timestamps (EVR).
VME system was a huge success, which can be upgraded to switch-based communication such as ATCA/microTCA.

## Slide 14
Motivation:
Hardware for CSNS-II
Based on the ATCA mechanical architecture,
Integrating functions of fast protection, timing, beam loss configuration, and data readout.
The front-end electronics for beam loss via SFP at superconducting cavities,
Real-time beam loss data with high-precision timestamps.
Master logic board
Interface board
Interface board
Interface board
Interface board
Interface board
5 Gbps
250 MHz
Customized Backplane & RTM
Approach: ATCA + FPGA + Rocket I/O
6U ATCA

## Slide 15
Rocket I/O
5 Gbps
Self-developed backplane with signal interfacing
6# slot
1#slot
3# slot
LVDS
250 MHz
Master: slot #3, while slave: slots #1, #2, #4, #5, and #6.
Master slot is responsible for logical processing, parameter configuration, status readback, and on-board IOC.
Slave slots handle external signal input and internal signal output.
Master slot is directly connected to each slave slot via 40 pairs of high-speed differential signals through pin-to-pin routing on the backplane.
24
16
Backplane board for CSNS-II

## Slide 16
Master logic board
Interface board
Flexible & Scalability : Multi-channel / Homogeneous / Independent links
Stop current beam
Global_Timing
Interlock
Front boards for CSNS-II

## Slide 17
8 QSFP
RF Soc
Power
K7
Si5395
FMC
DDR4
Low:200MHz,250MHz
High:2-2.5Gbps / 3-4 3-10 5Gbps
Front boards : Master logic board (in progress)

## Slide 18
Front boards : Master logic board (in progress)
the PCB layout
3D view
QSFP
(64*SFP)
7V690T
ZU47DR
（Embedded IOC）
4 QSFP + 1 PCIE
Event timing support
HPC FMC
8x 14 bits ADC, 5 GSPS, 6GHz analog BW
8 x 14 bits DAC, 10 GSPS, 4GHz analog BW
Megtron-6, 24 Layer
5*40
SFP for EVR
HPC FMC
PCIE
5*TE
DC12V
AD/DA
Power tree 02
Power tree 01

## Slide 19
Front boards : Interface board (in progress)
Opt-type input : HFBR2412T => 74ALVC164245 =>FIN1027AMX(LVTTL to LVDS) => TE
PLC-type input : phoenix => FOD060L => 74ALVC164245=>FIN1027AMX(LVTTL to LVDS) => TE
PLC-type output : TE => 830S21AMI-01LFT74ALVC164245(LVLLT to TTL) => MOC3063 => phoenix
Opt-type output : TE => 830S21AMI-01LFT(LVDS to LVLLT)=> 74ALVC164245=> HFBR1414T
1*40
1*40
6U ATCA
input
output
Self-developed backplane
Master board

## Slide 20
Principles and methods
Differential BCM system for SC Linac
DBCM(SNS)
commissioning(laboratory)
Synchronously acquire bunch-by-bunch BCM waveform (14-bit, 5 Gbps).
Analysis and decision-making, minimizing machine protection response.
Will implement an edge AI to determine the optimal timing for beam stop.
-- Graduate Research Topic

## Slide 21
Summary
Adopt ATCA architecture based on a customized backplane and self-developed front boards as the solution.
Using one main logic board (Embedded IOC) and four types of interface boards to cover most applications.
Integrating BLM and the FPS into a unified platform is challenging, and the real-data with high-precision timestamps is worthwhile to attempt (EVR function).
Combining DBCM with AI in the linear superconducting section are expected to further enhance the performance.
A significant amount of preliminary research and development work has been successfully completed.
New hardware circuits and algorithms have been proposed, and are being progressively verified and implemented.
The technological advancement offers an opportunity to enhance the operational performance of the upgrade.

## Slide 22: Thank you for your attention ！