## Slide 1
Mingtao Kang, Hong Chen
September 17th, 2025
The design and development of control system in the UTEF

## Slide 2
Outline
Requirements
Design and Status
  Data center: machine room, server cluster, storage and networking
  High-level applications(HLA)
  Low-level applications(LLA)
Prototype
  Electron gun test stand
  Magnetic field measurement
Plan
  Fast protection system
  Post-Mortem System
Summary

## Slide 3
Requirements
To perform basic control functions: device and instrument control, monitoring
To improve operation efficiency
To provide control, communication platform
To provide data archiving and database service
To provide scientific data storage

## Slide 4
Requirements
No. | System | Controlled devices | Qt. (sets) | Interface Type
1 | Electron gun | Electron gun | 1 | Modbus TCP/IP
2 | Radio frequency | Modulator | 5 | Modbus TCP/IP
3 |  | Water temperature | 78 | Wire
4 |  | Water flow | 78 | Wire
5 | Power supply | Power supply | 102 | Modbus TCP/IP
6 | Vacuum | Ion pump | 50 | RS-485 serial port
7 |  | Gauge | 14 | RS-485、wire
8 |  | Gate valve | 6 | Wire
9 | Beam diagnostics | BPM | 15 | Channel Access
10 |  | ICT | 4 | Channel Access
11 |  | Beam profile | 17 | Channel Access
12 |  | Energy spread | 2 | Channel Access
List of controlled devices for injector in phase I

## Slide 5
Requirements
No. | System | Controlled devices | Qt. (sets) | Interface Type
1 | Pulse power supply | Pulse power supply | 1 | Modbus TCP/IP
2 | Power supply | Power supply | 175 | RS-485 serial port
3 | Vacuum | Ion pump | 95 | RS-485 serial port
4 |  | Gauge | 12 | RS-485、wire
5 |  | Gate valve | 10 | Wire
6 | Beam diagnostics | BPM | 27 | Channel Access
7 |  | Beam profile | 2 | Channel Access
8 |  | DCCT | 1 | Channel Access
9 |  | Synchronized light profile | 1 | Channel Access
10 |  | BXB feedback | 1 | Channel Access
11 |  | Collimator | 2 | Channel Access
12 |  | BCM | 1 | Channel Access
13 | Insertion Device | Insertion Device | 1 | Modbus TCP/IP
List of controlled devices for storage ring in phase I

## Slide 6
PLC
Visualize
Computer
Industrial controller
Serial port server
RTOS
File Server
Web Server
Database Server
Application Server
SAN Storage
Operator Consoles
Large Display
Timing
Electron Gun Cooling Water
Vacuum、MPS
Pulse Power Supply Power Supply
Vacuum
Instrument
Vacuum
High-Speed Gigabit Network
Control Network
EPICS 7
HTTP
Wire & industry ethernet
C++
State Notation Language
Customized Development
Architecture/Design and Status

## Slide 7
xFusion tower server
H3C for networking
PLCs for electron gun, vacuum, cooling water, interlocks
Beijer touch screen for PLCs
MRF EVG/EVR for timing system with cPCI modules
Motion controller and driver
Industrial controller for instrument
Hardware/Design and Status

## Slide 8
Subystem/Design and Status
Data center
  Machine room
  Servers cluster
  Storage
  Networking
High-level applications
  Archiver appliance, alarm, clog, related database, etc.
  Scientific data storage
Low-level applications
    Electron gun
    Timing
    Vacuum
    Cooling water
    Power Supply/pulse power supply
    Machine protection
    Beam diagnostics
    Insertion device
    Instrument control and monitoring

## Slide 9
Machine Room/Data center
  The floor space: 50㎡
    18 racks(Server, Storage, Networking...resources)
  IT Load
    Dual power supply: UPS + Civil power supply
    Each power supply can afford all the IT loads
  Dual power supply:
    From two independent transformers to improve stability
  Total Power Capacity: 100kW
  UPS
    Modular equipment: expandable
    Total capacity:10KVA
    Backup time: 0.5 hour

## Slide 10
Server Cluster and storage/Data center
  The central computer system is a large and complex infrastructure.
  It consists of servers computers disk arrays client terminals and so on.
  PVE virtualization server cluster
  Development, applications
  Relational database, network management
  Data archiving and viewer, alarm management
  Error logging, logging services and IOC booting.
No. | computing | Storage | comments
1 | 3*24 Core | Disk:3*4*16=192TB | Installed
2 | 6*24 Core | Disk:6*4*16TB | To be installed

## Slide 11
Server cluster and storage/Data center
Console and Proxmox Virtual
Environment (PVE) GUIs

## Slide 12
Networking/Data center
2-layer intranet network structure
distribution layer
access layer
100Gb/s link
40Gb/s link
1Gb/s link

## Slide 13
Software tools/HLA
EPICS Base7.0.2 as overall software platform
CS-Studio "Phoebus" and QT as OPI development tool
MySQL for RDB based Apps
Debian 11/12 Linux for OS
Python/MATLAB scripting support
Proxmox VE for virtualization

## Slide 14
EPICS IOCs
Technical Systems
EPICS IOC
Soft Records
（run control, etc.)
Machine Learning Data mining …
Physics Applications, Beam Study Tools
Save/Compare/Restore,
Archiving, Post Mortem System, …
Matlab-Python-EPICS 7 Toolkit
Naming &
Directory
Service
Component
DB
Infrastructure
Monitoring
Database
Display Manager
Historian
data
Save/Set/
Restore
Alarm
Service
olog
collaborate with the EPICS Community
Others
EPICS Extensions
Phoebus, alh, StripTool, …
EPICS 7
HTTP
Network
Architecture/HLA

## Slide 15
High-level applications
Archiver appliance GUI
Clog GUI

## Slide 16
Timing System/LLA
Event timing adopt by many synchrotron light sources.
Performance and functionality are pretty well for synchrotron light source applications.
Storage Ring
Linac
Notes: Select event system are very nature!

## Slide 17
Timing System/LLA
Provide timing for accelerator systems, beamlines and experiments
  Provide accurate timing sequences to trig e-Gun, klystrons, injection, ramping, extraction, etc.
  synchronizing clocks to beam instrumentations, power supplies, beam-line experiments, etc.
  Provide timestamps to most equipment controls
Overall time accuracy better than 10ns, critical equipment can reach 10 ps accuracy

## Slide 18
Power supply Control/LLA
Based on PVE virtual machine to implement the communication protocol between the IOC and the power supply interface board.
distribution layer
access layer
Server
PS
PS
PS
PS
PS
Backup server
PVE cluster
…
40G Ethernet
1G Ethernet
Server
Backup server
…

## Slide 19
Vacuum Control/LLA
Development of PLC interlock program completed
Software design and development for touch panel in good progress.

## Slide 20
Machine Protection System/LLA
In order to prevent damage to accelerator components in case of failure, highly reliable Machine Protection System(MPS) is indispensable.
it can deliver less than 20 msec reaction time, and guarantee UTEF running safely and easy to operate, set the machine modes together with Personnel Protection System(PPS).

## Slide 21
Electron gun test stand/Prototype
Electron Gun | Siemens PLC(Ethernet)->IOC | Tested
Cooling water，valve interlock，machine protection | Yokogawa FA-M3 PLC(backplane)-> Yokogawa RP61(IOC) | Tested
Vacuum Pump, vacuum gauge | Vacuum Pump(RS485)->IOC Vacuum gauge(RS485)->IOC | Tested
Power supply | Power supply (Ethernet)->IOC | Tested
Beam Image | Camera(Ethernet)->IOC | Tested with Camera and Python
DAQ | Channel access | Tested
Summary for EPICS and Device interface of electron gun test stand

## Slide 22
Electron gun test stand/Prototype
Console
Electron gun OPI

## Slide 23
Electron gun test stand/Prototype
Timing OPI
Fluorescent target OPI

## Slide 24
Electron gun test stand/Prototype
Power supply OPI
2 archiver appliances status OPIs
Pcaspy-based IOC

## Slide 25
Electron gun test stand/Prototype
Archiver appliances and Clog GUI by workstation

## Slide 26
Magnetic field measurement/Prototype
Magnetic field measurement GUI based QT for python
MySQL for RDB based Apps
Magnetic field measurement and database using MySQL GUI

## Slide 27
Fast Protection system/Plan
Timing system
EVR
MPS system
PLC
Fast event
(Trip RF signal)
Actuator
(RF station)
Timing system
EVR
MPS system
PLC
Fast Protection system
Slow Protection system
Timing system can be used to transmit fast event to actuator.
  EVR modules have uplink event generation capability.
  Fan out concentrator modules can concentrate signals form eight EVRs/downstream and forward the signals upstream.
  EVG module has external input to enable 8 event triggers.

## Slide 28
Post-Mortem System/Plan
Important tool to analyze the cause of beam trip
  Generation and distribution of the trigger signal
  Storage of relevant signals
  RF, BPM, PS, etc.
  Data Recorder
  BPM platform, Oscilloscope, Data Recorder, etc.

## Slide 29
Summary
Controls overall architecture set
Timing work started
Early database work in progress
High-level application framework and platform set
The overall system is going ahead in good progress with no obvious barriers
The rest work is scheduled properly
Still further tight cooperation with the other systems is needed to push the whole work forward

## Slide 30
THANK YOU！
All Suggestions are welcomed！