## Slide 1: ALICE DETECTOR CONTROL SYSTEM Presented at RT 2009, Beijing
Peter Chochula, Lennart Jirden, Andre Augustinus, Lionel Wallet, Marco Bocciolli, Peter Rosinsky, Giacinto de Cataldo, Cesar Torcato,Luis Granado
CERN - ALICE
ALICE

## Slide 2
Experiment
Size: 16 x 26 meters (some detectors >100m away from IP)
Weight: 10,000 tons
Detectors: 18
Magnets: 2
Dedicated to study of ultra relativistic heavy ions collisions at LHC
Collaboration
Members: 1000
Institutes: 90
Countries: 30
ALICE DCS PROJECT
Started 8 years ago
Small central team collaborating with:
  Detector groups (~100 people involved)
  LHC experiments
ALICE DCS
Responsible for safe 24/7 operation of ALICE
Based on commercial SCADA system PVSSII
Controls 18 sub-detectors and about 150 subsystems (HV,LV,FEE…)
Provides infrastructure and services for the experiment

## Slide 3: (Some of the) alice detectors

## Slide 4
Very High Voltage (100 kV) 25um HV membrane
High Voltage (3 kV)
Low Voltage (60 kW)
Front-End Electronics
Mounted on chambers
Cooling 0.1 oC stability
Gas (88 m3)
510 cm
  l = 5.1 m, d = 5.6m
  570 k readout channels
  Largest Ever
ALICE TPC

## Slide 5
Inner Tracking System
~ 10 m2 Si detectors, 6 layers
Pixels, Drift, double sided Strips
3.9 cm < r < 43 cm
Strip layers
Drift layers
Pixel layers
Pb-Sn solder bumps: ~30µm diameter
Readout chips: 725mm native thickness
thinned to 150mm after bump deposition
10 000 000 pixels, configured via DCS
ALICE Inner Tracking System (ITS)

## Slide 6
Installation of the ITS in ALICE

## Slide 7
~ 8 m2 PbW04 crystals,
r ~ 5m
Operating at -20C
18 k channels controlled and configured via DCS
Photon Spectrometer

## Slide 8
4 RPC trigger planes, 120 m2,
20 k FEE
Muon Spectrometer
10 CSC tracking planes, 90 m2,
1.1 M FEE

## Slide 9
TPC Readout Partition
Examples:
ALICE TPC
4500 Front End cards
>500 000 channels
ALICE TRD
>1 000 000 readout channels
250 000 tracking CPUs configured via DCS
Frontend and readout electronics – new type of challenge for the DCS
    unlike in the past, DCS is now involved in configuration and control of large number of FEE modules
FEE cards often mounted directly on detectors
Large number of Ethernet ports required directly on detectors
    more than 700 SBCs in ALICE DCS
    operation in magnetic field
TPC
TRD

## Slide 10
Detector Controls System
DETECTORS
External Services and Systems
Electricity
Ventilation
Cooling
Gas
Magnets
Safety
Access Control
LHC
Configuration
Database
Archival
Database
Devices
Devices
Devices
Devices
SCADA
1000 ins/s
Up to 6GB
Infrastructure
B-field
Space Frame
Beam Pipe
Radiation
Envitonment
Alice Systems
DAQ
TRIGGER
HLT
Conditions
Database
ECS
OFFLINE
SPD
PHO
FMD
T0
V0
PMD
MTR
MTK
ZDC
ACO
SDD
SSD
TPC
TRD
TOF
HMP
Controls Context

## Slide 11
GAS
COOLING
HV
LV
FEE
ALICE on-detector electronics
Detector devices
DCS data storage
(ORACLE, fileservers)
Data Consumers
Offline
(GRID)
Operator UIs
DCS data processing farm
LHC
Magnets
Safety
FEE
External sub-systems
300 000 values/s
read by software
30 000 values/s
Injected into PVSS
1000 values/s
Written to ORACLE after smoothing in PVSS
>200 values/s
Sent to consumers
Dataflow in ALICE DCS
  6GB of data is needed to fully configure ALICE for operation
  Several stages of filtering applied to acquired data

## Slide 12: Building blocks of ALICE DCS
HVPS
LVPS
FEE
…
18 detectors with different requirements
  Effort to device standardization
    Still large diversity mainly in FEE part
      Large number of busses (CANbus, JTAG, Profibus, RS232, Ethernet, custom links…)
1200 network-attached devices
270 crates (VME and power supplies)
4 000 controlled voltage channels

## Slide 13
HVPS
LVPS
FEE
…
DEVICE ACCESS and ABSTRACTION
Device DRIVER
Device DRIVER
Device DRIVER
Device DRIVER
OPC SERVER
OPC SERVER
FED SERVER
FED SERVER
180 000 OPC items
100 000 Front-End (FED) services
1 000 000 parameters supervised by the DCS
Monitored at typical rate of 1Hz
Hardware diversity is managed through standard interfaces
  OPC servers for commercial devices
  FED servers for custom hardware
    Provides hardware abstraction, uses CERN DIM (TCP/IP based) protocol for communication

## Slide 14
CENTRAL SYSTEMS
DETECTOR SYSTEM
DETECTOR SYSTEM
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
HVPS
LVPS
FEE
…
DEVICE ACCESS and ABSTRACTION
Device DRIVER
Device DRIVER
Device DRIVER
Device DRIVER
OPC SERVER
OPC SERVER
FED SERVER
FED SERVER
Core of the DCS is based on commercial SCADA system PVSSII
110 detector computers
60 backend servers
DCS Oracle RAC (able to process up to 150 000 inserts/s)
BACKEND SYSTEMS
DNS
FS
MON
RAC
ACC

## Slide 15: PVSSII Architecture
      PVSSII system is composed of specialized program modules (managers)
      Managers communicate via TCP/IP
      ALICE DCS is built from 100 PVSS systems composed of 900 managers
      PVSSII is extended by JCOP and ALICE frameworks on top of which User applications are built
CTL
API
DM
EM
DRV
DRV
DRV
UI
UI
UI
User Application
ALICE Framework
JCOP Framework
PVSSII

## Slide 16
User Interface
Manager
Data
Manager
Driver
Driver
Driver
User Interface
Manager
User Interface
Manager
Event
Manager
API
Manager
Control
Manager
In a scattered system, the managers can run on dedicated machines
In a simple system all managers run on the same machine

## Slide 17
Distribution
Manager
Distribution
Manager
Distribution
Manager
User Interface
Manager
Data
Manager
Driver
Driver
Driver
User Interface
Manager
User Interface
Manager
Event
Manager
API
Manager
Control
Manager
User Interface
Manager
Data
Manager
Driver
Driver
Driver
User Interface
Manager
User Interface
Manager
Event
Manager
API
Manager
Control
Manager
User Interface
Manager
Data
Manager
Driver
Driver
Driver
User Interface
Manager
User Interface
Manager
Event
Manager
API
Manager
Control
Manager
In a distributed system several PVSSII systems (simple or scatered) are interconnected

## Slide 18
CENTRAL SYSTEMS
DETECTOR SYSTEM
DETECTOR SYSTEM
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
HVPS
LVPS
FEE
…
DEVICE ACCESS and ABSTRACTION
Device DRIVER
Device DRIVER
Device DRIVER
Device DRIVER
OPC SERVER
OPC SERVER
FED SERVER
FED SERVER
Each detector DCS is built as a distributed PVSSII system
  Mesh, no hierarchical topology
  Detector specific

## Slide 19
CENTRAL SYSTEMS
DETECTOR SYSTEM
DETECTOR SYSTEM
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
HVPS
LVPS
FEE
…
DEVICE ACCESS and ABSTRACTION
Device DRIVER
Device DRIVER
Device DRIVER
Device DRIVER
OPC SERVER
OPC SERVER
FED SERVER
FED SERVER
ALICE DCS is built as a distributed system of detector systems
Central servers connect to ALL detector systems
    global data exchange
    synchronization
    Monitoring…

## Slide 20
PVSS
CENTRAL SYSTEMS
DETECTOR SYSTEM
DETECTOR SYSTEM
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
HVPS
LVPS
FEE
…
DEVICE ACCESS and ABSTRACTION
Device DRIVER
Device DRIVER
Device DRIVER
Device DRIVER
OPC SERVER
OPC SERVER
FED SERVER
FED SERVER
OPERATIONS LAYER
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
PVSSII distributed system is not a natural system representation for the operator
ALICE DCS Is modeled as a FSM using CERN SMI++ tools
  Hide experiment complexity
  Focus on operational aspect

## Slide 21
DET1
HV
LV
FEE
…
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
DCS
DET1
VHV
HV
LV
…
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
Hierarchical approach:
  ALICE DCS is represented as a tree composed of detector systems
  Each detector system is composed of subsystems
  Subsystems are structured to devices (crates, boards) and channels

## Slide 22
DET1
HV
LV
FEE
…
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
DCS
DET1
VHV
HV
LV
…
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
SINGLE CHANNEL FSM
OFF
STB
ON
CFG
RAM
UP
RAMP
DWN
ERR
CONFIGURE
GO_ON
GO_OFF
RESET
GO_STB
(simplified) TOP LEVEL FSM
STB
BEAM
Tuning
READY
Moving BT
Moving
Ready
Moving
BT
ERR
GO_BT
GO_RDY
GO_STB
RESET
GO_BT
DCS devices are described as FSM
State diagrams are standardized for channels and devices of the same type
Top level DCS takes into account status of all leaves

## Slide 23
DET1
HV
LV
FEE
…
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
DCS
DET1
VHV
HV
LV
…
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
Top level DCS state is computed as a combination of all FSM states
Single channel can affect the top level state (hence the readiness of the whole DCS)

## Slide 24
DET1
HV
LV
FEE
…
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
DCS
DET1
VHV
HV
LV
…
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
DCS operator can exclude any part of the DCS tree and release the control to other users
Top level DCS does not take excluded parts of the hierarchy into account

## Slide 25
DET1
HV
LV
FEE
…
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
DCS
DET1
VHV
HV
LV
…
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
Subsystem expert can take control and take care of the problem
Excluded parts of the hierarchy can be returned to the central operator on fly

## Slide 26
PVSS
CENTRAL SYSTEMS
DETECTOR SYSTEM
DETECTOR SYSTEM
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
HVPS
LVPS
FEE
…
DEVICE ACCESS and ABSTRACTION
Device DRIVER
Device DRIVER
Device DRIVER
Device DRIVER
OPC SERVER
OPC SERVER
FED SERVER
FED SERVER
OPERATIONS LAYER
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH

## Slide 27
PVSS
CENTRAL SYSTEMS
DETECTOR SYSTEM
DETECTOR SYSTEM
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
PVSS
HVPS
LVPS
FEE
…
DEVICE ACCESS and ABSTRACTION
Device DRIVER
Device DRIVER
Device DRIVER
Device DRIVER
OPC SERVER
OPC SERVER
FED SERVER
FED SERVER
OPERATIONS LAYER
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
CH
UI LAYER

## Slide 28
DCS UI
  ALICE component used by all detectors
  Standardized operation representation
  Detector specific panels
    Central operator can browse and operate detector panels
Central panel
FSM operation
Detector Panel
DCS tree
Detector systems are developed by detector teams outside CERN
More than 100 integration session were organized with individual detectors
Verification of:
  Conformity to rules (naming conventions, interfaces, …)
  Stability
  Performance
  Safety (interlocks, alerts…)
  Dataflow (configuration, archival)
  Security (access control)
  Common operation with ALICE
Common sessions with all ALICE detectors

## Slide 29
First tracks seen at LHC and
recorded by ALICE SPD during injection line tests
June 15, 2008
First beams injected to LHC and steered 3km around LHC, passing ALICE
8.8.2008 around 8pm (Beijing time)
… which triggered worldwide celebrations
(Beijing, 8.8.2008 around 8pm)

## Slide 30
First beams circulating LHC
10, September 2008
Luminosity monitor (V0)
… and seen by ALICE DCS
… which was READY

## Slide 31: Conclusions
ALICE DCS is built on commercial software (PVSS, OPC) with CERN extensions (Framework, SMI++, DIM, FED servers…)
Large distributed PVSS system operates according to specifications
ALICE DCS was READY for LHC beams in 2008
Looking forward for physics in 2009