## Slide 1: OPERATION & MAINTENANCE RECORD (KSTAR Helium Refrigeration System)
Dong-Seong Park, Ph.D. (Principal Engineer),
on behalf of
Vacuum & Cryogenic Engineering Team
DEMO Technology Research Division
Advanced Technology Research Center
2018-06-05

## Slide 2
CONTENTS
1. INTRODUCTION
2. OPERATION SUMMARY
3. MAINTENANCE/REPAIR
4. SYSTEM MODIFICATION
5. SUMMARY

## Slide 3
INTRODUCTION

## Slide 4
INTRODUCTION
Introduction
Parameter | KSTAR | ITER
Major radius, R0 Minor radius, a Elongation,  Triangularity,  Plasma volume Plasma surface area Plasma cross section Plasma shape Plasma current, IP Toroidal field, B0 Pulse length N Plasma fuel Superconductor Auxiliary heating /CD Cryogenics | 1.8 m 0.5 m 2.0 0.8 17.8 m3 56 m2 1.6 m2 DN, SN 2.0 MA 3.5 T 300 s 5.0 H, D Nb3Sn, NbTi ~ 26 MW 9kW@4.5K 1kW@4.5K | 6.2 m 2.0 m 1.7 0.33 830 m3 680 m2 22 m2 SN 15 (17) MA 5.3 T 400 s ~2.0 H, D, T Nb3Sn, NbTi 73 (110) MW 3*25 kW@4.5K 1MW LN2 Plant
Mission of Program
- Korean Superconducting Tokamak Advanced Research
- Construct the superconducting tokamak
- Exploit SC tokamak operation technologies
Steady state H-mode operation
High performance operation modes
KSTAR Main Hall-2011
KSTAR Tokamak
NBI-1 (5MW)
NBI-2 (6MW)
Under commissioning
Fueling system
Diagnosis Systems
Vacuum Duct
Secondary helium distribution

## Slide 5
INTRODUCTION
History of Cryogenic Activity
1991
2002
2005
2006-2007
2008
2015
2017-Present

## Slide 6
INTRODUCTION
Cryogenic System Configuration
HELIUM REFRIGERATION SYSTEM
(9kW@4.5K, Air Liquide Advanced Technologies, 2008)
HELIUM DISTRIBUTION SYSTEM
CURRENT LEAD SYSTEM
KSTAR TF & PF SC MAGNETS SYSTEM
KSTAR CURRENT LEAD
GAS MANAGEMENT SYSTEM#2
HELIUM REFRIGERATOR
(1kW@4.5K, Linde Kryotechnik AG, 1st built 2002 & relocated/modified 2016)
UPGRADED DISTRIBUTION SYSTEM
CPI
NBI-2
SMBI
LHE DEWAR
(R&D USERS)
PIS
GAS MANAGEMENT SYSTEM#1

## Slide 7
INTRODUCTION
Process Diagram of KSTAR Helium Circuit w/ 9kW@4.5K

## Slide 8
Thermal damper
INTRODUCTION
SC magnet Cooling & Operation Trend
Thermal load handling of the KSTAR SC magnets
LHe supply
6.6bar
4.4K
4.4bar
5.5K
SHe circulator
4.4bar
4.4K
4.2bar
5.5K
4.2bar
4.5K
1.1 bar
1.3 bar
Cold compressor
4.3 K (1.1b) LHe
Magnet coil
Magnet str.
HX1
HX2
HX3
6.9bar
4.9K
 | TF Circulator | PF Circulator | Cold Comp.
Speed | 1,010 Hz | 1,010 Hz | ~235 Hz
dm/dt | 340 g/s | 372 g/s | ~300 g/s
△P | 2.4 bar | 2.0 bar | 0.2 bar
Pinlet | 6.6 bar | 6.2 bar | 1.1 bar
Poutlet | 4.2 bar | 4.2 bar | 1.3 bar
Bearing | Dynamic gas (Foil) |  | Ceramic ball
Operation of TF Circuit
Operation of PF Circuit

## Slide 9
OPERATION SUMMARY

## Slide 10
OPERATION SUMMARY
Cryoplant Operation Plan
Annual operation program (2017)
Month
12
4.5K
80K
300K
KSTAR Temp.
1
2
3
4
5
6
7
8
9
10
11
Cool-down
KSTAR Operation
Maintenance &
Campaign preparation
Warm-up
00
09
10
17
18
24
TF Coil Current
35 KA
-35 KA
0 KA
TF coil charge
TF coil discharge
TF ramp-up
TF ramp-down
Daily operation scenario
Maintenance &
Campaign preparation
20-25 shots per a day
3,000~4,000 hr operational
annually

## Slide 11
OPERATION SUMMARY
Plant Operation Times
2018

## Slide 12
OPERATION SUMMARY
Thermal Load into KSTAR HRS
 | Thermal load (peak, kW@4.5K) |  |  |  | 
 | Design | ‘09 | ‘10 | ‘11 | ’12-’16
Thermal shields | 1.5 | ~1.0 | ~1.0 | ~1.0 | ~1.0
TF+PF+SC BL | 5.7 | ~1.4 | ~2.6 | ~3.0 | ~3.2
Circulators |  | ~1.8 | ~1.8 | ~1.8 | ~1.8
Current leads | 1.8 | ~0.6 | ~1.0 | ~1.0 | ~1.0
Total | 9.0 | ~4.8 | ~6.4 | ~6.8 | ~7.0
Items |  | Contents
Electricity | 6.6 kV | 3,600 kW consuming
 | 380V-Non UPS | 100 kW installed
 | 380V-UPS | 60 kW installed
Cooling water | Tower water | 520 m3/h (32°C/37°C)
 | Chilled water | 25 m3/h (22°C/27°C)
Instrument air | Compressed air | 44 Nm3/h @ 8 bar
 | GN2 back-up | 650 Nm3/h @ 6 bar
CWS
Electricity
Utility Consumption

## Slide 13
OPERATION SUMMARY
Failure Record
Items |  | Count | Consequences | Remarks
1 | Oil pump | 23 | Unless redundancy ⟶ ESD | will be discussed later
2 | Utility failure | 7 | HRS ESD | Incl. micro power-cut
3 | Turbines | 4 | Cool-down interrupted | Solved
4 | Instrumentation | 3 | Valves fault | 
5 | Cold compressor | 2 | TD temp./press. rising | Solved
6 | Circulator | 5 | SHe supply decreased | Solved
7 | Vacuum system | 3 | No impact (∵prompt repair) | Solved
Total |  | 47 |  | 
Year | Reason of downtime
2008 | Oil pumps, electricity
2009 | T3
2010 | Oil pumps, electricity
2011 | Electricity, oil pumps
2012 | Electricity
2013 | None
2014 | T3 & UPS
2015 | Minors
2016 | Mechanical seal, Utilities failures, etc.
2017 | None
Availability≈95%
Availability of the KSTAR HRS

## Slide 14
MAINTNANCE/REPAIR

## Slide 15
MAINTENANCE/REPAIR
Maintenance Schedule & Summary
Item |  | Service period | Remarks
Warm compression system (WCS) | Screw compressor | 20,000 hr | Manufacturer
 | Electric motor | 15,000 hr | Manufacturer
 | ORS coalescing filter | 10 years | NFRI
 | ORS charcoal | 5 years | NFRI
 | Charcoal dust filter | 3 years | NFRI
 | Oil pump | 1 year | NFRI
 | Oil filter | 5 years | NFRI
 | Motor control center | 2 years | NFRI
Cold Box (C/B) | Expander#1-#3 | 1 year | NFRI
 | Expander#4-#6 | 2 years | NFRI
 | Vacuum system | 1 year | NFRI
 | Cryogenic valves | 5 years | NFRI
Distribution Box (D/B) | Cold compressor | 5,000 hr | Manufacturer
 | TF SHe circulator | 10,000 hr | Manufacturer
 | PF SHe circulator | 5,000 hr | Manufacturer
 | Cryogenic valves | 5 years | NFRI
Instrument | T, P, m sensor | 1 year | NFRI
 | PLC & control | 1 year | NFRI

## Slide 16
MAINTENANCE/REPAIR
Oil Removal System
Coalescing filter (2017)
- Oil contamination issues at the CRYO-OPS 2016/2014
- Coalescers visual inspection
26 October 2016
Item | Coalscer#1 | Coalscer#2 | Coalscer#3 | DCS | Remarks
Oil | Little wet | Dry, but little wet surface | Dry | Normal | 
Filter damage | No | No | No |  | 
Charcoal adsorber
- Activate charcoal exchange : 2009 & 2015
• Elapsed time ~2 weeks
• Utility
- GN2 : 200,000 Nm3
- GHe : ~600 Nm3

## Slide 17
MAINTENANCE/REPAIR
Cold Compressor
Failure trend@FY2010
 | 10/06, 13:00 | 10/07, 01:00 | 10/07, 13:00
Speed | 221 Hz | 172 Hz | 233 Hz
PInlet | 1.13 bar | 1.21 bar | 1.11 bar
Poutlet | 1.26 bar | 1.27 bar | 1.26 bar
Vibration | 4.57 μm | 20.41 μm | 11.52 μm
PLP_CS | 1.05 bar | 1.05 bar | 1.05 bar
Inspection at the manufacturer’s workshop
Used DL-2 Fluorine grease (IR)
New DL-2 Fluorine grease (IR)
- Suspected root cause was grease dry-out due to vacuum (< 1 mbar) while P/F
- Counter measures
1) Changed grease type from Fluorine base to Lithium base
2) Modify the conditioning procedure at lower vacuum (~100 mbar)
Vibration developing

## Slide 18
SYSTEM MODIFICATION

## Slide 19
SYSTEM MODIFICATION
Major System Modification List
Items | Contents | Result | Remarks
C/B Sensor Upgrade (2017) | • Temp. sensors redundancy • Using Cernox CU sensors | - Better reliability of C/B operation w/ redundant sensors of temperature | Refer to the poster of Mr. Jae-Joon JOO for the details
Internal circuit modification (2014) | • Remove heat-leak sources • D/B#1 internal piping modification | - No more SHe circuit fluctuation is observed - Better stability of the cryoplant | 
Control System Upgrade (2011-2018) | • Establish the PLC redundancy • WinCC S/W upgrade | - Better reliability & scalability of the plant operation | 
 | • Realize the cool-down autonomy by using cool-down record of past years | - Better stability & less HR input while cool- down period - Demonstrates proper cool-down autonomy | Refer to the poster of Mr. Kyung-Mo MOON for the details
 | • SHe circuit pressure load handling | - Reduce pressure loss in the TF/PF circuit - Mitigate the pressure head in the PF circuit | Will be resented at the following slide
C/B sensor upgrade
Internal Circuit Modification
Cool-Down Autonomy

## Slide 20
SYSTEM MODIFICATION
Pulsed (Pressure) Load Handling Control Logic
4.3 K (1.1b) LHe
Thermal damper
PF Magnet coil
PF Magnet str.
HX1
HX2
HX3
SHe filling
SHe venting
P
P
∆P
TF circulator (2011)
PF circulator (2011)
PF circulator
Cold
compressor
Control logic for entire SHe pressure handling
 NFRI original logic
Control logic for pressure head mitigation in the circuit
 Collaboration with ITER Organization
Real action movie

## Slide 21
SUMMARY

## Slide 22
SUMMARY
Operation
The KSTAR HRS has demonstrated sufficient cooling power with margin to cope with the
thermal load from KSTAR Tokamak
The KSTAR HRS has experienced 47 times of abnormal events while campaign period until now
The availability of system has been around 95% for past 30,000 hr operation
Plant Modification
The activities of system/component modification increased the reliability & stability of plant
Maintenance/Repair
The cryoplant has been operated properly thanks to successful maintenance/repair activities
Most of maintenance/repair works are performed by NFRI that helps the flexibility of operation

## Slide 23
谢谢您的倾听!!!
THANK YOU FOR THE ATTENTION!!!
경청해 주셔서 감사합니다!!!