## Slide 1: Commissioning and first operation of the XFEL cryogenic system
T. Schnautz
Deutsches Elektronen-Synchrotron (DESY), Hamburg, Germany
Notes: How to edit the title slide
Upper area: Title of your talk, max. 2 rows of the defined size (55 pt)
Lower area (subtitle): Conference/meeting/workshop, location, date, your name and affiliation, max. 4 rows of the defined size (32 pt)
Change the partner logos or add others in the last row.

## Slide 2: Overview
Overview:
General information about XFEL project
XFEL refrigerating plant
  HERA refrigerating plant XFEL refrigerating plant
  Commissioning of XFEL refrigerating plant
  Performance results
  Cold compressors
    Operational experiences
    Bypass operation
    2K pressure stability
    Cold compressor lifetime problems
    Recovery after shutdown (e.g. bearing failure)
Summary
Overview of XFEL cryogenic equipment
Notes: Before you start editing the slides of your talk change to the Master Slide view:
Menu button “View” > Slide Master:
Edit the following items:
1. On the Title slide (second master slide)
a) Click to add title of your talk
b) Click to add subtitle (conference, location, name of the speaker, date)
2. On the Slide Master (first master slide)
a) The 1st row in the violet header: Delete the existent text and write the title of your talk into this text field b) The 2 rows in the footer area: Delete the text and write the information regarding your talk (same as on the Title Slide) into this text field.
If you want to use more partner logos position them left beside the DESY logo in the footer area.
Close Master View

## Slide 3: European XFEL Project
  XFEL:
  Length of accelerator: 1500m
  Length of facility: 3400m
  Accelerator modules : 96
  Design electron energy: 17.5 GeV
  Start of beam operation: January, 2017
  Start of user runs: September, 2017
  Electron energy in October, 2017: 14.9 GeV
  SASE-Operation of all three undulators with variable bunch pattern
  Beam operation with 5000 bunches / sec with high intensity of X-ray laser
  XFEL enables simultaneous provision of different experiments with various and high puls-rates
  XFEL cryogenic system:
671 control valves
2647 temperature sensors
800 pressure sensors
212 flow sensors
>100 level sensors
433 regulation loops
> 22000 records
> 220000 properties

## Slide 4: European XFEL Project
8 cavities + sc Quadrupole = 12m Cryomodule
768 superconducting 9-cell 1.3 GHz cavities
Helium II bath cooling at 2.0 K - 5/8K and 40/80K thermal shields
European XFEL Project

## Slide 5: XFEL cryogenic system Overview
XFEL
FLASH
Former HERA

## Slide 6: XFEL cryogenic system Overview
SC
SC
SC
SC
SC
SC
SC
SC
Contributions
LINDE
Coldbox 41
Coldbox 43
XFEL-Subplant 41
XFEL-Subplant 43
SC
SC
SC
SC

## Slide 7: XFEL cryogenic system Overview
SC
SC
SC
SC
SC
SC
SC
SC
Contributions
LINDE
Coldbox 41
Coldbox 43
XFEL-Subplant 41
XFEL-Subplant 43
SC
SC
SC
SC
To be modified
To be removed
No changes
LN2 heat exchanger removed
Re-arrangement of expansion turbines
50% of piping modified

## Slide 8: XFEL cryogenic system Overview
SC
SC
SC
SC
SC
SC
SC
SC
Contributions
LINDE
Coldbox 41
Coldbox 43
XFEL-Subplant 41
XFEL-Subplant 43
SC
SC
SC
SC
XFEL-Purifier

## Slide 9: XFEL cryogenic system Overview
Contributions
LINDE
SC
SC
SC
SC
SC
SC
SC
SC
Distribution Box
DB54
Coldbox 41
Coldbox 43
SC
SC
SC
SC
XFEL-Purifier

## Slide 10: XFEL cryogenic system Overview
Distribution Box
XLVB
Contributions
LINDE
DEMACO
BINP
Warm
He-Pumps
SC
SC
SC
SC
SC
SC
SC
SC
Distribution Box
DB54
Cold Compressors
CB44
XRTL
(Building 54)
Cryo Plant
Shaft
AMTF
Coldbox 41
Coldbox 43
SC
SC
SC
SC
XFEL-Purifier

## Slide 11: XFEL cryogenic system Overview
Contributions
LINDE
DEMACO
BINP
Linac
Warm
He-Pumps
SC
SC
SC
SC
SC
SC
SC
SC
Distribution Box
DB54
Cold Compressors
CB44
Distribution Box
XLVB
XRTL
(Building 54)
Cryo Plant
Distribution Box
XLVB
Shaft
Distribution Box
XLVB
CM
FC
EC
3,9 GHz
Injector
CM
FC
EC
3,9 GHz
AMTF
Coldbox 41
Coldbox 43
SC
SC
SC
SC
XFEL-Purifier

## Slide 12: XFEL cryogenic system Overview
Contributions
LINDE
DEMACO
BINP
Linac
Warm
He-Pumps
SC
SC
SC
SC
SC
SC
SC
SC
Distribution Box
DB54
Cold Compressors
CB44
Distribution Box
XLVB
XRTL
(Building 54)
Cryo Plant
Distribution Box
XLVB
Shaft
Distribution Box
XLVB
CM
FC
EC
3,9 GHz
Injector
CM
FC
EC
3,9 GHz
AMTF
Coldbox 41
Coldbox 43
SC
SC
SC
SC
XFEL-Purifier
Main Linac
CMS
FC
EC
CMS
FC
EC
CMS
SCB
EC
CMS
FC
SCB
FC: Feed cap
EC: End cap
CMS: Cryomodul string
SCB: String connection box
1
2
3

## Slide 13: XFEL cryo plant Cryo capacity
Croygenic plant-capacity: Performance requirements vs. performance results:
Parallel coldbox operation:
CB41 + CB43
Cooling loop | unit | DESY calculated | DESY specification (calculated + safety margin) | Linde offer (guaranteed) | Linde offer (expected) | Test results CB 41 + CB 43
2K | kW | 1.46 | 1.9 | 1.9 | 2.01 | > 1.9
5K – 8K | kW | 2.4 | 3.6 | 3.6 | 3.95 | 4.0
40K – 80K | kW | 16.0 | 24 | 24 | 26.12 | 25.9
Conclusion:
Guarantee values for parallel coldbox operation have been exceeded!
CB 41
CB 43
+

## Slide 14: XFEL cryo plant Cryo capacity
Cooling loop | unit | DESY calculated | DESY specification (calculated + safety margin) | Linde offer (guaranteed) | Linde offer (expected) | Test results CB 41
2K | kW | 1.46 | 1.9 | - | 2.01 | > 1.9
5K – 8K | kW | 2.4 | 3.6 | - | 3.03 | 2.74
40K – 80K | kW | 16.0 | 24 | - | 20.2 | 18.14
Conclusion:
Single coldbox operation is sufficient for operation of XFEL
CB 41
Single coldbox operation:
CB41
Croygenic plant-capacity: Performance requirements vs. performance results:

## Slide 15: First cooldown Linac
XFEL Linac
First cooldown:
10.12.2016
27.12.2016
Start asymmetrical operation of two coldboxes to speed up cooldown
Recovery of cold return flows in cold-boxes to enhance cryogenic capacity
Fast cooldown at temperatures below liquid nitrogen (no more thermal stress)
Cooldown with one coldbox
300 K
4 K

## Slide 16: Cold compressors Operational challenges
Cold compressors are very sensitive towards massflow-, pressure- and temperature-changes in the 2K-return flow
  Massflow (-stability) is most important
  Required massflow has to be “produced”
Cold compressors: Operational challenges:
Small dynamic range for operation
  Designed for one special working point
  Deviations from this working point have to be compensated to avoid shutdown
Ideal operating field
Cold compressors
CB44
XFEL
Linac & Injector
XFEL
Refrigerating plant
2K return flow

## Slide 17: Cold compressors Operational challenges
Cold compressors are very sensitive towards massflow-, pressure- and temperature- changes in the 2K-return flow
  Massflow(-stability) is most important
  Required massflow has to be “produced”
Cold compressors: Operational challenges:
Small dynamic range for operation
  Designed for one special working point
  Deviations from this working point have to be compensated to avoid shutdown
Surge line
    Choke operation: Should be avoided as cryo capacity decreases
XFEL
Refrigerating plant
Cold compressors
CB44
XFEL
Linac & Injector
XFEL
Refrigerating plant
2K return flow
    Surge operation: Not possible. Crossing the surge line …
        breakdown of operation
        unnecessary loads on cold compressor motors
        unnecessary downtime (5-8 hours recovery time)

## Slide 18: Cold compressors Requirements on XFEL cold compressors
Requirements on XFEL cold compressors:
2K Pressure stability: < 2%
High availability (Exchange of cold compressor motors for maintenance after 16.000hrs)
Reduction of recovery time
Stand alone operation & re-connection of XFEL Linac/injector at sub atmospheric pressure
Cold compressors
CB44
CC-bypass
XFEL
Linac & Injector
XFEL
Refrigerating plant
Cold compressor bypass system can fulfill these requirements
Massflow compensation avoid CC-shutdowns caused by heat load changes
Suction pressure: 24mbar - 1000mbar
  30% turn down capacity (by reducing the suction pressure of warm screw compressors)
Notes: Before you start editing the slides of your talk change to the Master Slide view:
Menu button “View” > Slide Master:
Edit the following items:
1. On the Title slide (second master slide)
a) Click to add title of your talk
b) Click to add subtitle (conference, location, name of the speaker, date)
2. On the Slide Master (first master slide)
a) The 1st row in the violet header: Delete the existent text and write the title of your talk into this text field b) The 2 rows in the footer area: Delete the text and write the information regarding your talk (same as on the Title Slide) into this text field.
If you want to use more partner logos position them left beside the DESY logo in the footer area.
Close Master View

## Slide 19: Cold compressors Bypass operation
Bypass operation: Massflow compensation, temperature adjustment & stand alone operation
2K supply
(~4.5K)
2K supply (linac)
Cold compressors (require ~110g/s)
Cold compressor bypass
Mass flow compensation
Temperature adjustment
Stand alone operation
Cold compressor bypass functions:

## Slide 20: Cold compressors Bypass operation
2K supply
(~4.5K)
2K return (linac)
2K supply (linac)
2K return flow: 70g/s
Cold compressors (require ~110g/s)
Bypass operation: Massflow compensation, temperature adjustment & stand alone operation

## Slide 21: Cold compressors Bypass operation
2K supply
(~4.5K)
2K return (linac)
2K supply (linac)
20K return
(coldbox)
2K return flow: 70g/s
Cold compressors (require ~110g/s)
Bypass operation: Massflow compensation, temperature adjustment & stand alone operation

## Slide 22: Cold compressors Bypass operation
2K supply
(~4.5K)
2K return (linac)
2K supply (linac)
20K return
(coldbox)
CC-bypass has to produce: 40g/s
2K return flow: 70g/s
Cold compressors (require ~110g/s)
Bypass operation: Massflow compensation, temperature adjustment & stand alone operation

## Slide 23: Cold compressors Operational experiences - bypass operation
2K supply
(~4.5K)
2K return (linac)
2K supply (linac)
20K return
(coldbox)
CC-bypass has to produce: 40g/s
2K return flow: 70g/s
CC inlet temperature is adjusted by use of two heat exchangers in CC-bypass
Real CC mass flow: 2K return flow + CC-bypass flow
Cold compressors (require ~110g/s)
Bypass operation: Massflow compensation, temperature adjustment & stand alone operation

## Slide 24: Cold compressors Bypass operation
Bypass operation: Massflow compensation
Massflow bypass
22.02.2017 (12:00)
25.02.2017 (10:00)
110 g/s
50 g/s
60 g/s
Required massflow
Real massflow = (2K return flow + bypass flow)
2K return flow (linac & injector)
Bypass flow
20.03.2017 (06:00)
20.03.2017 (12:00)
110 g/s
50 g/s
60 g/s
Required massflow
Real massflow
Bypass flow
2K return flow
Surge shutdown
Conclusion:
CC-bypass operation delivers reasonable reactions on changes in 2K return flow

## Slide 25: Cold compressors 2K pressure stability
31mbar
29mbar
Pressure linac
Set-pressure linac
Pressure CC-inlet
Set-pressure CC-inlet
Cold compressors: 2K Pressure stability
    Cascaded pressure regulation “CPR” (DESY)
Cold compressors
CB44
XFEL
Linac & Injector
1.5km
Pressure controller CC
Set pressure CC-inlet: dynamic
Output
Input
Pressure controller linac
Set pressure linac: 31mbar
  Event in linac reaches cold compressors with certain delay
  Situation/condition in linac can differ from situation at inlet of CCs
Use of pressure controller linac: CC-surges can be created!
Both pressure controllers should be used for pressure adjustment in 2K circuit (cascaded regulation)!
Use of pressure controller CC: 2K Pressure stability in linac may not be satisfying!
Pressure controller CC
Set pressure CC-inlet: 31mbar – pressure drop
Pressure controller linac
Set pressure linac: 31mbar
?
?
    Improvement of 2K pressure stability
    - could be demonstrated by Linde
    ü
    Specified pressure stability: < 2% (31 mbar +/- 0.6 mbar)

## Slide 26: Cold compressors Operational experiences – 2K pressure stability
Cold compressors: 2K Pressure stability
    Specified pressure stability: 2% (31 mbar +/- 0.6 mbar) could be demonstrated by LKT
1% - pressure stability
2K pressure
  30.9 mbar
  30.3 mbar
  30.6 mbar
Required massflow for CCs
Real massflow
(2K return flow + bypass massflow)
2K return flow from linac
Massflow bypass
05.04.2017 (09:00)
05.04.2017 (16:00)
05.04.2017 (09:00)
05.04.2017 (16:00)
Conclusion:
Cold compressors deliver a 2K pressure stability better than 2%.
“CPR” and “AHLC” improve the 2K pressure stability significantly to 0.3%!
Sudden RF-shutdown
(10 GeV)
Sudden RF-shutdown
(10 GeV)
    Automatic heat load compensation “AHLC” (DESY): Changes in the 2K return flow – caused by dynamic RF operation - are determined automatically and compensation takes place in the linac by automatic heating in the 2K liquid helium.
    Talk by J. Penning
    Improvement of 2K pressure stability
    Cascaded pressure regulation “CPR” (DESY)

## Slide 27: Cold compressors Motor failures
Conclusion:
Downtime, caused by cold compressor issues, has to be reduced significantly
  Duration of interruption in case of motor failure: at least 30 hours (for cryo group)
New CC-motor design has to be developed soon to …
  … match the specified lifetime
  … guarantee reliable XFEL user operation
  Problem solving related to lifetime of CC-motors is ongoing
  Definition of a design-upgrade is in progress
Root cause analysis by Linde Kryotechnik
Current problems/challenges with cold compressors: CC-motor failures
CC-motors are equipped with ceramic ball bearings
Motors show systematic bearing problems
Specification: lifetime of cold compressor motors of at least 16000 hrs.
Due to the bearing failures, the specified lifetime could not yet be demonstrated
2018: Two XFEL user-runs had to be interrupted caused by bearing damages
900h < lifetime of bearings < 9000h

## Slide 28: Cold compressors Recovery after shutdown (e.g. bearing failure)
Cold compressors
CB44
CC-bypass
XFEL Coldbox
Distribution box
XLVB
Warm He pumps
AMTF
XFEL
Linac & Injector
Normal operation configuration
29mbar
1000mbar
2K return flow
Recovery after shutdown (e.g. bearing failure)

## Slide 29: Cold compressors Recovery after shutdown (e.g. bearing failure)
Cold compressors
CB44
CC-bypass
XFEL Coldbox
Distribution box
XLVB
Warm He pumps
AMTF
XFEL
Linac & Injector
1000mbar
1000mbar
29mbar
1000mbar
Sudden shutdown (e.g. bearing failure)
Operation configuration after surge – beam operation not possible, but linac can be kept cold at 31mbar
2K return flow
Recovery after shutdown (e.g. bearing failure)

## Slide 30: Cold compressors Recovery after shutdown (e.g. bearing failure)
Cold compressors
CB44
CC-bypass
XFEL Coldbox
Distribution box
XLVB
Warm He pumps
AMTF
XFEL
Linac & Injector
1000mbar
29mbar
1000mbar
Operation configuration after surge – beam operation not possible, but linac can be kept cold at 31mbar
Warm up
Exchange of CC-motor
Pump & purge
Stand alone operation
Cool down
Internal pump down (< 29mbar)
2K return flow
Recovery after shutdown (e.g. bearing failure)

## Slide 31: Cold compressors Recovery after shutdown (e.g. bearing failure)
Cold compressors
CB44
CC-bypass
Recovery after shutdown (e.g. bearing failure)
XFEL Coldbox
Distribution box
XLVB
Warm He pumps
AMTF
XFEL
Linac & Injector
< 29mbar
1000mbar
29mbar
1000mbar
Normal operation configuration after internal pumpdown and re-connection of XFEL linac/injector
Re-connection of linac at sub atmospheric pressure
2K return flow

## Slide 32: Cold compressors Recovery after shutdown (e.g. bearing failure)
Switch XFEL linac from cold compressors to warm He pumps
Warm up of cold compressors
Exchange of CC-motor
Pump & purge
Stand alone operation
Cool down of cold compressors
Prepare for pump down
Strat internal pump down (< 29mbar)
Start connection of cold compressors to XFEL Linac
  Open cold compressor inlet valves
  Re-connect XFEL linac at sub atmospheric pressure
  Prepare for process stabilization
  Create sufficient return flow from linac (e.g. by heating)
Start cascaded regulation for pressure adjustment
Start heat load compensation
Stabilize operation
Sequence for recovery after shutdown (e.g. bearing failure)
Procedure has been automated by DESY for 99% to save time and personal!
Permanently adapt parameter to current situation

## Slide 33: Summary
XFEL cryogenic system: Summary
  The 2K pressure stability is excellent (0.3%)
  The cascaded pressure regulation in combination with the automatic heat load compensation improved the pressure stability significantly
  Even dynamic procedures (power ramping, rf-shutdown, etc.) can be compensated quite well without affecting the pressure stability drastically
The recovery effort after a cold compressor shutdown (e.g. bearing failure) is minimized by …
  … the possibility of the stand alone CC-bypass operation and
  … the automation of the recovery procedure
  The commissioning of the XFEL cryo plant (4K) was successful
    The performance results comply with the specification
  The first cooldown of the XFEL linac/injector was successful
    No major problems occurred (e.g. cold leaks)
  The bearing problems of the cold compressor motors are not yet solved
  Many theories were discussed, some of them were identified as relevant
  Improvements since commissiong – but general problem still has to be solved
    A new motor design has to be developed soon to guarantee reliable XFEL user operation

## Slide 34: Cold compressors
Thank you for your attention