## Slide 1
Performance degradation of helium refrigerator for cryogenic hydrogen system at J-PARC
T. Aso, M. Teshigawara, S. Hasegawa, H. Muto, K. Aoyagi, H. Takada
J-PARC Center
Japan Atomic Energy Agency
4-7 June 2018
IHEP
Just dismantled ADS

## Slide 2
Oil based troubles in other facilities
・Degradation of cooling power from 2005
(AIP Conf. Proc. 1218, pp.1410-1417, 2010)
(2) CERN: CMS refrigerator
Capacity: 620 W@4.5K
He flow: 140 g/sec
Capacity: 1.5 kW@4.5K
He flow: 220g/sec
Commissioning in 2004
・Amount of oil : ～2 kg
・Concentration : 750 ppm
(Cryo-Ops 2016)
2015 degradation
・Amount of oil : 375 g
・Concentration : <10 ppb
In our case, it occurred even small amount of oil accumulation.
・Large amount of oil released from compressor
・Accumulated oil inside heat exchanger
(1) RIKEN: Cryogenic cooling system for SRC
It works well up to now

## Slide 3
Contents
Outline of J-PARC
Outline of cryogenic hydrogen system
Performance degradation of refrigerator
Investigations of cause
Measures for performance degradation
Consideration
Present status of pressure drop
Summary

## Slide 4
1. Outline of high-intensity neutron source at J-PARC
Materials and Life Science Experimental Facility
Linac
3GeV Synchrotron
50GeV Synchrotron
Hadron Experimental Facility
Neutrino Beams to Kamioka
300m
Pacific ocean
J-PARC (Japan Proton Accelerator Research Complex)
Spallation neutron source
→ Cold neutron
using by refrigerator
Operation started since 2008
Current beam power is 500 kW

## Slide 5
2. Outline of cryogenic hydrogen system
Hydrogen circulation system
Helium refrigerator Cold box
Cascade refrigeration system of helium and hydrogen for cooling neutrons
Hydrogen circulation system | 
Pressure | 1.5MPa
Temperature (moderator inlet) (moderator outlet) | 18K 21K
Flow rate | 180g/s
Helium refrigerator | 
Pressure | 1.6MPa
Flow rate | 270g/s
Capacity | 6kW at 17K
・Operation period: 60-100days/cycle, Current operating time : 50,000 hrs.
・1st ADS : Replacement at 12,000 hrs.
・2nd ADS : Pressure drop appeared at 18,000 hrs. since 2015.
→ Performance degradation

## Slide 6
Heat exchangers
ADS
HX2 outlet temperature
Jan. 2015
Jan. 2015
Apr. 2015
Apr. 2015
Jan. 2015
Apr. 2015
Nov. 2014年
Apr. 2014
Nov. 2014
Apr. 2014
Nov. 2014
Apr. 2014
Feb. 2015
Mar. 2015
Oct. 2015
Nov. 2015
Feb. 2015
Mar. 2015
Oct. 2015
Nov. 2015
Oct. 2015
Mar. 2015
Nov. 2015
Feb. 2015
ΔP1
T
ΔP2
Since 2015,
・Pressure drop increased with every operation.
・Pressure drop of ADS was 7-8 times larger than
one of heat exchangers.
・Outlet temperature of HX2 was also increased.
Finally, liquid hydrogen could not be generated.
・Pressure drop was reset by warm-up
3. Performance degradation of refrigerator

## Slide 7
2015.1
Operating time of refrigerator （hrs)
Heat exchanger (HX1+HX2)
ＡＤＳ
Impurity concentration (ppm)
Remaining N2 of active charcoal regeneration process
Q-mass (2015.11)
4. Investigations of cause
(1) Impurity measurements by gas chromatograph
almost < 1ppm
ADS: N2 = 10-100ppm
→within design value

## Slide 8
4. Investigations of cause
2016.1
Mass to charge ratio (m/z, a.m.u.)
Pressure (Pa)
ADS
Background
HX
LP line
H2O
N2
CO2
He
(2) Impurity measurements by Q-mass
After operation,
measured area partitioned by valves
Almost background → No impurity

## Slide 9
2016
2017
2018
Oil concentration (ppb)
Operating time of compressor (hrs)
○ 270g/s
● 200g/s
At outlet of OS-5
He flow rate
・Cold trap extraction using liquid N2
・Infrared spectroscopy analysis
・ ~10 ppb
・ Equivalent to
design value
(3) Oil concentration measurement by cold trap
4. Investigations of cause

## Slide 10
(4) Observation of inlet of HX-1
4. Investigations of cause
with ultra violet light
with ultra violet light
Fiber scope
Fiber scope
No oil and contamination

## Slide 11
(1) Cleaning of inside heat exchangers
(2) ADS replacement
5. Measures for performance degradation
Heat exchanger removal from cold box, and cleaning by Freon
Replacement work in cold box
From results of the cause investigation,
・No impurities
・Low oil concentration (~10 ppb)
However, measures for oil accumulation

## Slide 12
HX-1
HX-2
HX-3
Measure of accumulated oil inside heat exchangers
0.18g/350mL(AK-225G）
・Total oil collection: 95.1 g
・Circulation cleaning of Freon (AK-225G, 480 litters)
・Target：No.1 and 2 heat exchangers
・Non-volatile residue

## Slide 13
Inlet
Outlet
Just after dismantled ADS (He inlet side)
・ Surface (3 mmt) of upper felt was yellowed
・ Oil was accumulated in membranous form
Pressure drop
Felt
・Both sides of charcoal to hold it
・High siliceous glass fiber （12 mm thickness）
・8 layer laminated
Activated charcoal
( Oil freezes and disturbs He flow …)

## Slide 14
Oil distribution in ADS
Area |  | Oil content (wt%) | Oil content (g) | Total (g)
Upstream Felt | 1 | 14±0.14 | 17.7 | 45.6
 | 2 | 8.8±0.20 | 11.1 | 
 | 3 | 6.7±0.31 | 8.5 | 
 | 4 | 4.4±0.01 | 5.6 | 
 | 5 | 0.99±0.03 | 1.3 | 
 | 6 | 0.63±0.04 | 0.8 | 
 | 7 | 0.39±0.04 | 0.5 | 
 | 8 | 0.09 | 0.1 | 
Charcoal | Up. | 0.020±0.003 | 0.8 | 2.1
 | Mid. | 0.014±0.002 | 0.6 | 
 | Lo. | 0.016±0.001 | 0.7 | 
Downstream Felt | 1 | 0.16 | 0.2 | 0.3
 | 2 | 0.04 | 0.05 | 
 | 3 | <0.01 | 0.01 | 
 | 4 | <0.01 | 0.01 | 
 | 5 | <0.01 | 0.01 | 
 | 6 | <0.01 | 0.01 | 
 | 7 | <0.01 | 0.01 | 
 | 8 | <0.01 | 0.01 | 
 |  |  | Total | 48.0
He outlet
He inlet
Upstream Felt
Activated charcoal
Downstream Felt
Felt played a role of filter
layer
Example of RIKEN (g)
5.1
111.9
0.8
First ADS (g)
0.04
-
-
High siliceous glass fiber
Rock wool
・ADS accumulated oil : 48.0 g
・HX(95g) + ADS(48g) = 143 g
Comparable: ~10ppb x 20000hr
95% of oil was trapped at upstream felt

## Slide 15
Flowing element test of the felt
Element test was carried out to confirm the pressure drop due to the accumulated oil on the felt.
・Case: with/without oil case
・Flow; Nitrogen gas
Temperature: 150K
Pressure: 0.3MPa
Mass flow rate: 8.3-14.8 Nm3/h
・Cooling by liquid nitrogen
With oil case increased
differential pressure.

## Slide 16
8. Consideration
・ ADS : Pressure drop occurred due to accumulated oil on surface of felt
・ Pressure drop at ADS was 7-8 times larger than that at HX.
・ Pressure drops occurred same time at ADS and HX.
・ HX :
→ We don’t understand
that large pressure drop of ADS affected on the performance of the HX.

## Slide 17
Operating time (days)
Pressure drop (kPa)
7. Present status of pressure drop
2012.4-6
2017.10-12
2018.1- ->
2015.10-11
2012.4-6
2017.10-12
2018.1- ->
2015.10-11
HX1+HX2
ADS
・No pressure drop increase
・No performance degradation
Performance has been recovered
July
July

## Slide 18
9. Summary
Although amount of oil accumulation at ADS and HX was small,
(Oil concentration in He was within design value,)
performance degradation of refrigerator was occurred.
We are still making effort to investigate the cause.
Cause of large pressure drop at ADS was due to oil on surface of felt.
→ Improvement of ADS by changing felt
It’s under consideration whether large pressure drop at ADS affected performance degradation of HX.
Thank you for your attention