## Slide 1: Summary of Session 5 Other Vibration Source
Masaru Takao
JASRI

## Slide 2: Session 5: Other Vibration Source
S. Matsui (RIKEN)
Effect on Beam Orbit Stability of Ground Motion and Vacuum Chamber Vibration Caused by Cooling Water System at the SPring-8 Storage Ring
J. Zhang (IHEP)
Optimization Design of the Vibration Isolation of AC magnet Girder

## Slide 3: Summary of Talk given by Matsui 1
Measurement of floor vibration of SPring-8 SR
  Source of floor vibration: cooling system

## Slide 4: Summary of Talk given by Matsui 2
Propagation path of vibration to tunnel:
〇 floor, X cooling water pipe

## Slide 5: Summary of Talk given by Matsui 3
Propagation path of vibration to beam:
〇 vacuum chamber vibration,
X magnet vibration

## Slide 6: Summary of Talk given by Matsui 4
Cooling water also vibrate vacuum chamber.

## Slide 7: Summary of Talk given by Matsui 5
Eddy current induced by Al vacuum chamber vibration.
Kick field of Eddy current generated due to asymmetric cross section of vacuum chamber.

## Slide 8: Summary of Talk given by Matsui 6
Experimentally confirmed equivalence of vacuum chamber and magnet vibration

## Slide 9: Summary of Talk given by Matsui 7
Suppression of beam oscillation:
Additional support to vacuum chamber.

## Slide 10: Summary of Talk given by Zhang
AC magnet in RCS vibrates itself.
The precision of the magnets iron core is the most important factor to the vibration problem.
To reduce the vibration, study the isolation, or dumping system for girder of AC magnet.
Comments:
  Seek dumping material,...
  In case of eigen frequency known, there may be effective method.