## Slide 1: Green CEPC
Zhenchao LIU
On behalf of CEPC working group
2018.11.14

## Slide 2: Content
Why Green CEPC
Green Technology for large colliders
Green CEPC
More collaboration is needed with industries and institutes

## Slide 3: Why Green CEPC
China is reducing energy pollution, promoting green travel and boosting unit energy GDP
Huge energy is needed for modern large colliders such as LHC, ILC, CEPC…
Huge energy means huge cost and huge pollution!!!
Power consuming: CEPC is about 1.5LHC
Green CEPC ~ lower cost for unit data! Exciting!!!
Saving power=lower pollution=lower operation cost!!!

## Slide 4: Power for Large Colliders
300MW is the upper limit for wall plug power of such large projects
Operation cost: 1kWh~0.5RMB，266MW x 24h x 200day x 0.5RMB = 638.4MRMB = 96.67M US dollar
Chart: Projects
| CEPC@H | CEPC@W | CEPC@Z | CERN | FCC-ee@350GeV | FCC-hh@100TeV | ILC@1TeV | ILC@500GeV
 | 266.032 | 223.212 | 148.772 | 180 | 354 | 468 | 300 | 164

## Slide 5: Green Technology for large colliders

## Slide 7: Renewable Energy
ILC, ESS

## Slide 8: High efficiency klystron
70% can be reached, 80% still need to develop

## Slide 9: Reuse of klystron waste power

## Slide 10: High Q0 cavity

## Slide 11: HTS cable

## Slide 12: Green CEPC
Renewable energy
High efficiency power supply
High Q0 cavity
Reuse of waste heat
Cooling by environment

## Slide 13: CEPC power budget（H）
 | System for Higgs （30MW） | Location and electrical demand(MW) |  |  |  |  |  | Total (MW)
 |  | Ring | Booster | LINAC | BTL | IR | Surface building | 
1 | RF Power Source | 103.8 | 0.15 | 5.8 |  |  |  | 109.75
2 | Cryogenic System | 11.62 | 0.68 |  |  | 1.72 |  | 14.02
3 | Vacuum System | 9.784 | 3.792 | 0.646 |  |  |  | 14.222
4 | Magnet Power Supplies | 47.21 | 11.62 | 1.75 | 1.06 | 0.26 |  | 61.9
5 | Instrumentation | 0.9 | 0.6 | 0.2 |  |  |  | 1.7
6 | Radiation Protection | 0.25 |  | 0.1 |  |  |  | 0.35
7 | Control System | 1 | 0.6 | 0.2 | 0.005 | 0.005 |  | 1.81
8 | Experimental devices |  |  |  |  | 4 |  | 4
9 | Utilities | 31.79 | 3.53 | 1.38 | 0.63 | 1.2 |  | 38.53
10 | General services | 7.2 |  | 0.2 | 0.15 | 0.2 | 12 | 19.75
 | Total | 213.554 | 20.972 | 10.276 | 1.845 | 7.385 | 12 | 266.032

## Slide 14: CEPC power budget（W）
 | System for W | Location and electrical demand(MW) |  |  |  |  |  | Total (MW)
 |  | Ring | Booster | LINAC | BTL | IR | Surface building | 
1 | RF Power Source | 103.8 | 0.15 | 5.8 |  |  |  | 109.75
2 | Cryogenic System | 5.94 | 0.41 |  |  | 1.72 |  | 8.07
3 | Vacuum System | 9.784 | 3.792 | 0.646 |  |  |  | 14.222
4 | Magnet Power Supplies | 23.35 | 5.52 | 1.75 | 0.5 | 0.12 |  | 31.24
5 | Instrumentation | 0.9 | 0.6 | 0.2 |  |  |  | 1.7
6 | Radiation Protection | 0.25 |  | 0.1 |  |  |  | 0.35
7 | Control System | 1 | 0.6 | 0.2 | 0.005 | 0.005 |  | 1.81
8 | Experimental devices |  |  |  |  | 4 |  | 4
9 | Utilities | 26.24 | 2.92 | 1.38 | 0.58 | 1.2 |  | 32.32
10 | General services | 7.2 |  | 0.2 | 0.15 | 0.2 | 12 | 19.75
 | Total | 178.464 | 13.992 | 10.276 | 1.235 | 7.245 | 12 | 223.212

## Slide 15: CEPC power budget（Z）
 | System for Z-pole | Location and electrical demand(MW) |  |  |  |  |  | Total (MW)
 |  | Ring | Booster | LINAC | BTL | IR | Surface building | 
1 | RF Power Source | 57.1 | 0.15 | 5.8 |  |  |  | 63.05
2 | Cryogenic System | 2.91 | 0.31 |  |  | 1.72 |  | 4.94
3 | Vacuum System | 9.784 | 3.792 | 0.646 |  |  |  | 14.222
4 | Magnet Power Supplies | 9.52 | 2.14 | 1.75 | 0.19 | 0.05 |  | 13.65
5 | Instrumentation | 0.9 | 0.6 | 0.2 |  |  |  | 1.7
6 | Radiation Protection | 0.25 |  | 0.1 |  |  |  | 0.35
7 | Control System | 1 | 0.6 | 0.2 | 0.005 | 0.005 |  | 1.81
8 | Experimental devices |  |  |  |  | 4 |  | 4
9 | Utilities | 19.95 | 2.22 | 1.38 | 0.55 | 1.2 |  | 25.3
10 | General services | 7.2 |  | 0.2 | 0.15 | 0.2 | 12 | 19.75
 | Total | 108.614 | 9.812 | 10.276 | 0.895 | 7.175 | 12 | 148.772

## Slide 16: CEPC power budget
 | System for Higgs （30MW） | Location and electrical demand(MW) |  |  |  |  |  | Total (MW)
 |  | Ring | Booster | LINAC | BTL | IR | Surface building | 
1 | RF Power Source | 103.8 | 0.15 | 5.8 |  |  |  | 109.75
2 | Cryogenic System | 11.62 | 0.68 |  |  | 1.72 |  | 14.02
3 | Vacuum System | 9.784 | 3.792 | 0.646 |  |  |  | 14.222
4 | Magnet Power Supplies | 47.21 | 11.62 | 1.75 | 1.06 | 0.26 |  | 61.9
5 | Instrumentation | 0.9 | 0.6 | 0.2 |  |  |  | 1.7
6 | Radiation Protection | 0.25 |  | 0.1 |  |  |  | 0.35
7 | Control System | 1 | 0.6 | 0.2 | 0.005 | 0.005 |  | 1.81
8 | Experimental devices |  |  |  |  | 4 |  | 4
9 | Utilities | 31.79 | 3.53 | 1.38 | 0.63 | 1.2 |  | 38.53
10 | General services | 7.2 |  | 0.2 | 0.15 | 0.2 | 12 | 19.75
 | Total | 213.554 | 20.972 | 10.276 | 1.845 | 7.385 | 12 | 266.032 (86.522, 32.5%)
Some power can use the renewable power such as wind, water, solar…
20% of wind power is wasted in China each year, price of wind power is the same as coal power at 2020.

## Slide 17: Wind power in China
In 2017, the total installed capacity of wind power in China reached 159 million kilowatts, accounting for 9.50% of the total installed power of the country. The on-grid power was 271.7 billion kilowatt hours, accounting for 4.76% of the country's total power generation.

## Slide 18: Wind power cost
Price of wind power will decrease year by year as technology development
266MW wind power station will cost 957.6MRMB~1.5year operation cost(638.4MRMB)
The construction period is short. A 10,000-kilowatt wind farm is built less than one year
No resources, no pollution
Installed capacity flexible, Actual footprint is small
图片来源：电气专业混编

## Slide 19: Wind power in Hebei
河北省发改委网站发布《河北省2018—2020年分散式接入风电发展规划》，确定了11市重点发展区域
  2018—2020年，全省规划开发分散式接入风电430万千瓦；展望至2025年，力争累计达到700万千瓦。
  石家庄：根据土地、电网条件落实情况，规划开发规模46.6万千瓦，2020年前开发规模41.1万千瓦，晋州、深泽、无极等县为重点开发区域，其余5.5万千瓦2025年前开发。
  保定：根据土地、电网条件落实情况，分散接入风电规划开发规模25.4万千瓦，2020年前开发规模19.2万千瓦，高阳、博野、安国、涞源等县（市）可作为重点开发区域，其余6.2万千瓦2025年前开发。
  沧州：根据土地、电网条件落实情况，分散式接入风电规划开发规模138万千瓦，2020年前开发规模103.8万千瓦，其余34.2万千瓦2025年前开发。
  衡水：根据土地、电网条件落实情况，分散式接入风电规划开发规模71.5万千瓦，2020年前开发规模42.7万千瓦，景县、枣强、武邑、饶阳、安平、武强等县可作为重点开发区域，其余28.8万千瓦2025年前开发。

## Slide 20
CEPC Power for Higgs & Z
266MW
149MW
The maximum power consumption is RF power source system.

## Slide 21
Power consumption
The Collider beam power is more than 60 MW. Wall plug power consumption is more than 100MW. The increase in efficiency of RF power sources is considered a high priority issue.
 | Tetrodes | IOTs | Klystrons | SSA | Magnetrons
 | DC–400MHz | (200–1500)MHz | 300 MHz – 1 GHz | DC – 20 GHz | GHz range
 | 1 MW | 1.2 MW | 1.5 MW |  | < 1MW
 | 85% - 90% (class C) | 70% | 65% | 60% | 90%
Remark | Broadcast technology, widely discontinued |  |  |  | Oscillator, not amplifier!
RF power sources - efficiencies
High power klystrons are the more attractive choice because of their high eﬃciency, low cost and more stable than IOT and SSA for CEPC collider.

## Slide 22
CEPC at 800 RMB/MWh and 6000 hours/year
Excessive electricity bill, M RMB
1 year
Efficiency, %
90 M RMB
130M RMB
Efficiency impact on operation cost (Only considering operation efficiency of klystrons)
NOW
COMING
FUTURE
Save Money
Power consumption

## Slide 23
1st tube: All drawings of the 1st prototype has finished and it has been processed and manufactured in the machine shop.
R&D Progress on High efficiency klystron
23
The three different schemes for the high efficiency klystron design are ongoing simultaneously.
The manufacturing of the 2nd prototype will be started based on the most mature scheme as soon as possible.

## Slide 24: SRF cavities for CEPC：High Q (= Low Power Loss & Energy-saving!)
24
 | Cavity amount | Gradient (MV/m) | Q for long period | Gradient in horizontal test (MV/m) | Q in horizontal test | Gradient in vertical test (MV/m) | Q in vertical test
650 MHz 2-cell cavity | 240 | 19.7 | 1.5E10 | 22 | 2E10 | 22 | 4E10
1.3 GHz 9-cell cavity | 96 | 19.8 | 1E10 | 22 | 2E10 | 24 | 3E10
1.3 GHz 9-cell cavity
650 MHz 2-cell cavity

## Slide 25: High Q achieved in the vertical test!
25
Vertical test result: Q0=4.0E10@19.2MV/m，which is close to the CEPC target (Q0=4.0E10@22.0MV/m).
Vertical test result: Q0=5.1E10@26.0MV/m，which exceed the CEPC target (Q0=4.0E10@22.0MV/m).
650 MHz 1-cell cavity (only BCP, no EP)
650 MHz 2-cell cavity (only BCP, no EP)

## Slide 26: N-doping: increase Q further!
26
CEPC Target
After N-doping, Q0 increased obviously at low field for both 650 MHz 1-cell cavities (650S1#, 650S2#).
650S1: Q0=7e10@Eacc=10MV/m. But Q0 decreased quickly at high field (>10 MV/m) because of no BCP/EP after N-doping.
650S2: Quench at Q0=6.9e10@Eacc=8.8MV/m.
Next, increase Q at high field for CEPC TDR.

## Slide 27: Nb3Sn film: Lower cavity loss significantly——Effort to TDR!
27
Vertical test results of 1.3GHz @ Cornell
Nb3Sn: high Tc, much higher Q than Nb at 4.2K, higher gradient (120MV/m in theory) than Nb (50 MV/m). Nb cavity coating with Nb3Sn film is promising in future. Related research has begun at IHEP. The furnace for Nb3Sn coating is under fabrication now.
Q of Nb3Sn: 30 times higher than Nb !
Parameters | Value
Min vacuum | 5.0E-5 Pa
Max temperature | 1400℃
Min vacuum@1400℃ | 9.0E-4 Pa
Uniform temperature area | Φ300mm×500mm
Furnace for Nb3Sn coating

## Slide 28: More collaboration with industries and institutes

## Slide 29: Energy R&D
The development of accelerator is limited by energy consumption, or say as the cost.
Energy design should be included in the accelerator design for the huge accelerator projects.
Energy source, recycle, efficiency, reuse should be consider together.
Waste water, gas, heat and the environment…

## Slide 30: CEPC power budget（H）
 | System for Higgs （30MW） | Location and electrical demand(MW) |  |  |  |  |  | Total (MW)
 |  | Ring | Booster | LINAC | BTL | IR | Surface building | 
1 | RF Power Source | 103.8 | 0.15 | 5.8 |  |  |  | 109.75
2 | Cryogenic System | 11.62 | 0.68 |  |  | 1.72 |  | 14.02
3 | Vacuum System | 9.784 | 3.792 | 0.646 |  |  |  | 14.222
4 | Magnet Power Supplies | 47.21 | 11.62 | 1.75 | 1.06 | 0.26 |  | 61.9
5 | Instrumentation | 0.9 | 0.6 | 0.2 |  |  |  | 1.7
6 | Radiation Protection | 0.25 |  | 0.1 |  |  |  | 0.35
7 | Control System | 1 | 0.6 | 0.2 | 0.005 | 0.005 |  | 1.81
8 | Experimental devices |  |  |  |  | 4 |  | 4
9 | Utilities | 31.79 | 3.53 | 1.38 | 0.63 | 1.2 |  | 38.53
10 | General services | 7.2 |  | 0.2 | 0.15 | 0.2 | 12 | 19.75
 | Total | 213.554 | 20.972 | 10.276 | 1.845 | 7.385 | 12 | 266.032 (171.65, 64.5%)

## Slide 31: Major power consumption area
RF and Magnet power supply consume 64.5% of the total power!!!
The energy transmit efficiency is very important for such power supplies.
Institute and industry should work together to develop the related technology.
RF power supply >80%
Magnet power supply???

## Slide 32: Thanks!