## Slide 1: Fault investigation tools at the ALBA synchrotron light source
Ferran Fernandez
ARW2019
Notes: ALBA is a third generation synchrotron light source near Barcelona (Spain). In operation for users since 2012, we aim at continuously improve the beam availability by increasing the mean time between failures (MTBF) and decreasing the mean time to recover (MTTR). In order to reduce the MTTR a good set of tools to quickly diagnose what has caused the incidence is a must. From the timing or PLC logs to the BPMs buffers; here we report our sources of information to investigate the failures. But, it’s not only a matter of having the information, but being able to quickly access to it. Thus, the Operator oriented tools to extract the data in the Control Room will also be presented. Finally different examples of failures will be given to illustrate our means and a list of "what we would like to have" will be discussed.

## Slide 2: Outline
Introduction
Sources of information
“Operator friendly” tools to get the data
Wishlist
Examples: Fail Modes Simulator
2
Notes: asdfasdf

## Slide 3: Introduction
BOOSTER
100 MeV – 3 GeV
STORAGE RING
3 GeV
LINAC
100 MeV
+ 8 Beamlines
+ 4 BLs in construction

## Slide 4: Introduction
4
Chart: Year
| 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019
Mean Time Between Failures | 20.75 | 24.95 | 33.7 | 51.38 | 58.2 | 111.97 | 91.7 | 92.83
Availability | 0.77 | 0.838 | 0.968 | 0.973 | 0.976 | 0.987 | 0.982 | 0.9757
Chart: Year
| 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019
Mean Time to Recover | 1 | 0.79 | 1.08 | 1.36 | 1.39 | 1.47 | 1.67 | 1.92

## Slide 5: Introduction
5
Tango Control System
Equipment Protection System
Machine Protection System
Magnets & PS
DI
RF
BPMs
CCG, IP, TC, Valves
Cooling
ID
PERSONAL SAFETY SYSTEM

## Slide 6: Sources of information
6
ARCHIVING
ONLINE DATA TO BE SAVED
FAST ARCHIVING
&
ONLINE DATA AUTOMATICALY SAVED

## Slide 7: Sources of information
7
ARCHIVING
Control system variables that are recorded periodically or “on change”
“Large” time resolution: from 1s to 1min typically
12 “kattributes” being recorded (600 Gb/month)
Easily accessible through the same GUIs as the control system, however...

## Slide 8: Sources of information
8
ARCHIVING
Power supplies: current, voltage,…
Vacuum: pressures, valves state, thermocouples,…
RF: forward/reverse power, cavity voltage,…
Cooling: temperature, flow, pressure,…
Radiation monitors: dose rates, accumulated dose
Insertion devices: gap, phase, correction coils current,…
Diagnostics: BPMs, Beam Loss Monitors, tune, current, lifetime, filling pattern, emittance (pinhole),…

## Slide 9: Sources of information
9
ARCHIVING
Useful to see:
Which were the general conditions of the accelerator when an incident happen
Long term drifts

## Slide 10: Sources of information
10
BPMs FAST ARCHIVING
14days
BPMs at 10kHz
MADE IN OPERATIONS

## Slide 11: Sources of information
11
ONLINE DATA AUTOMATICALY SAVED
Timing logs (timestamps) saved during reset
PLC log files saved during the reset
SR correctors at 5kHz during the last 14s saved each time FOFB stops
RF Fast Interlock Module and LLRF buffer saved during reset

## Slide 12: Sources of information
12
ONLINE DATA TO BE SAVED
Data “generated” under certain conditions (typically a Beam loss) that is erased after a Reset. These are:
BPMs turn by turn data; 250000 turns buffer
Personal Safety System info shown in its panel (Rack in the Control Room)
Status messages from the devices (Ex.: PS leakage current ITLK)

## Slide 13: “Op. friendly” tools to get the data
13
The most important after a Beam Loss is to quickly access to the protection systems (MPS and EPS) data
  acopTrip.py
    Timing Logs (Orbit trip, RF, VC itlk and SCW quench)
    RF info(IOTs status and trips,RF Fast Interlock Module, RF EPS)
  EPS GUI
    Summarizes in one view the general status of the Equipment Protection Systems PLCs
MADE IN OPERATIONS

## Slide 14
Timing Log: Event description Local time Timestamp [ns] BPMs Interlock - SR S02 2019-05-19 02:20:31 213077001
RF Plant 14A Fast Interlock 2019-05-19 02:20:31 213080716
RF Plant 10B Fast Interlock 2019-05-19 02:20:31 213080796
RF Plant 6A Fast Interlock 2019-05-19 02:20:31 213081020
RF Plant 14B Fast Interlock 2019-05-19 02:20:31 213081044 RF Plant 10A Fast Interlock 2019-05-19 02:20:31 213081436 RF Plant 6B Fast Interlock 2019-05-19 02:20:31 213081628 RF Plant BO Fast Interlock 2019-05-19 02:20:31 213100786 BPMs Interlock - SR S15 2019-05-19 02:20:31 213641728 BPMs Interlock - SR S13 2019-05-19 02:20:31 213648204 BPMs Interlock - SR S16 2019-05-19 02:20:31 213648445 BPMs Interlock - SR S11 2019-05-19 02:20:31 213653464 BPMs Interlock - SR S01 2019-05-19 02:20:31 213655425 BPMs Interlock - SR S12 2019-05-19 02:20:31 213658363 BPMs Interlock - SR S07 2019-05-19 02:20:31 213659532 BPMs Interlock - SR S08 2019-05-19 02:20:31 213661478 BPMs Interlock - SR S03 2019-05-19 02:20:31 213675792 BPMs Interlock - SR S06 2019-05-19 02:20:31 213845733
06a (HVON, HVON) FIM: Timing, Revers Cavity, Forward Load EPS: no interlocks Tx01: FaultRfon {RFON is not enabled from EPS} Tx02: FaultRfon {RFON is not enabled from EPS} 06b (AUX, HVON) FIM: Timing, Revers Cavity, Forward Load EPS: no interlocks Tx01: not in operation Tx02: FaultRfon {RFON is not enabled from EPS} 10a (HVON, HVON) FIM: Timing, Revers Cavity, Forward Load EPS: no interlocks Tx01: FaultRfon {RFON is not enabled from EPS} Tx02: FaultRfon {RFON is not enabled from EPS} 10b (HVON, HVON) FIM: Timing, Revers Cavity, Forward Load EPS: no interlocks Tx01: FaultRfon {RFON is not enabled from EPS} Tx02: FaultRfon {RFON is not enabled from EPS}
acopTrip.py

## Slide 15
EPS GUI

## Slide 16
16
“Op. friendly” tools to get the data
BPMs postmortem: plotPM.m

## Slide 17
17
“Op. friendly” tools to get the data
BPMs & Correctors
Fast archiver matlab GUIs
Turn OFF SCW magnetic field
FOFB OFF -> BPMs change
FOFB ON -> CORR change

## Slide 18
18
LLRF Fast Data Logger

## Slide 19
BEAM CURRENT LOST
START
Example 1

## Slide 20
EPS
GUI
InfoTrip.py
PCGRID
Post Mortem
WHAT DO YOU WANT TO CHECK ?
What happened ?
NEXT
General water cooling trend
RF
GUI

## Slide 21
WHAT HAPPENED ?
RF Body Current
Beamline Ebutton
SR Kicker FAIL
SR Quad water ITLK
BPM FAIL
RF ARC CAVITY
CPCI REBOOT
SR Corr -> orbit -> Vacuum trip
SR QUAD CTRL FAILURE
Water cooling system fail

## Slide 22
Ex. 2
End

## Slide 23
TRY AGAIN

## Slide 24
BACK

## Slide 25
Timing Log: Event description Device description Local time Timestamp [ns] BPMs Interlock - SR S02 SR02/TI/EVR-CDI0201-A 2019-05-19 02:20:31 213077001
RF Plant 14A Fast Interlock SR14/TI/EVR-CRF1402-A 2019-05-19 02:20:31 213080716
RF Plant 10B Fast Interlock SR10/TI/EVR-CRF1002-A 2019-05-19 02:20:31 213080796
RF Plant 6A Fast Interlock SR06/TI/EVR-CRF0602-A 2019-05-19 02:20:31 213081020
RF Plant 14B Fast Interlock SR14/TI/EVR-CRF1401-A 2019-05-19 02:20:31 213081044 RF Plant 10A Fast Interlock SR10/TI/EVR-CRF1001-A 2019-05-19 02:20:31 213081436 RF Plant 6B Fast Interlock SR06/TI/EVR-CRF0601-A 2019-05-19 02:20:31 213081628 RF Plant BO Fast Interlock BO04/TI/EVR-CRF1602-A 2019-05-19 02:20:31 213100786 BPMs Interlock - SR S15 SR15/TI/EVR-CDI1501-A 2019-05-19 02:20:31 213641728 BPMs Interlock - SR S13 SR13/TI/EVR-CDI1301-A 2019-05-19 02:20:31 213648204 BPMs Interlock - SR S16 SR16/TI/EVR-CDI1601-A 2019-05-19 02:20:31 213648445 BPMs Interlock - SR S11 SR11/TI/EVR-CDI1101-A 2019-05-19 02:20:31 213653464 BPMs Interlock - SR S01 SR01/TI/EVR-CDI0101-A 2019-05-19 02:20:31 213655425 BPMs Interlock - SR S12 SR12/TI/EVR-CDI1201-A 2019-05-19 02:20:31 213658363 BPMs Interlock - SR S07 SR07/TI/EVR-CDI0701-A 2019-05-19 02:20:31 213659532 BPMs Interlock - SR S08 SR08/TI/EVR-CDI0801-A 2019-05-19 02:20:31 213661478 BPMs Interlock - SR S03 SR03/TI/EVR-CDI0301-A 2019-05-19 02:20:31 213675792 BPMs Interlock - SR S06 SR06/TI/EVR-CDI0601-A 2019-05-19 02:20:31 213845733 BPMs Interlock - SR S09 SR09/TI/EVR-CDI0901-A 2019-05-19 02:20:31 213852714 BPMs Interlock - SR S05 SR05/TI/EVR-CDI0501-A 2019-05-19 02:20:31 213860776 BPMs Interlock - SR S04 SR04/TI/EVR-CDI0401-A 2019-05-19 02:20:31 213863241 BPMs Interlock - SR S10 SR10/TI/EVR-CDI1001-A 2019-05-19 02:20:31 213864394 BPMs Interlock - SR S14 SR14/TI/EVR-CDI1401-A 2019-05-19 02:20:31 214381064
06a (HVON, HVON) FIM: Timing, Revers Cavity, Forward Load EPS: no interlocks Tx01: FaultRfon {RFON is not enabled from EPS} Tx02: FaultRfon {RFON is not enabled from EPS} 06b (AUX, HVON) FIM: Timing, Revers Cavity, Forward Load EPS: no interlocks Tx01: not in operation Tx02: FaultRfon {RFON is not enabled from EPS} 10a (HVON, HVON) FIM: Timing, Revers Cavity, Forward Load EPS: no interlocks Tx01: FaultRfon {RFON is not enabled from EPS} Tx02: FaultRfon {RFON is not enabled from EPS} 10b (HVON, HVON) FIM: Timing, Revers Cavity, Forward Load EPS: no interlocks Tx01: FaultRfon {RFON is not enabled from EPS} Tx02: FaultRfon {RFON is not enabled from EPS} 14a (HVON, OFF) FIM: Timing, Revers Cavity, Forward Load EPS: IOT2_WF_ALRM Tx01: FaultRfon {RFON is not enabled from EPS} Tx02: not in operation
BACK

## Slide 26
BACK

## Slide 27
BACK

## Slide 28
BACK

## Slide 29
BACK

## Slide 30
BEAM CURRENT LOST
START
Example 2

## Slide 31
EPS
GUI
InfoTrip.py
PCGRID
Post Mortem
WHAT DO YOU WANT TO CHECK ?
What happened ?
NEXT
RF
GUI
General water cooling trend

## Slide 32
WHAT HAPPENED ?
RF Body Current
Beamline Ebutton
SR Kicker FAIL
SR Quad water ITLK
BPM FAIL
RF ARC CAVITY
CPCI REBOOT
SR Corr -> orbit -> Vacuum trip
SR QUAD CTRL FAILURE
Water cooling system fail

## Slide 33
Ex. 3
End

## Slide 34
TRY AGAIN

## Slide 35
BACK

## Slide 36
Timing Log: Event description Device description Local time Timestamp [ns] BPMs Interlock - SR S12 SR12/TI/EVR-CDI1201-A 2015-03-19 16:14:00 348812922 RF Plant 10B Fast Interlock SR10/TI/EVR-CRF1002-A 2015-03-19 16:14:00 348816861 RF Plant 14A Fast Interlock SR14/TI/EVR-CRF1402-A 2015-03-19 16:14:00 348816941 RF Plant 6B Fast Interlock SR06/TI/EVR-CRF0601-A 2015-03-19 16:14:00 348817029 RF Plant 10A Fast Interlock SR10/TI/EVR-CRF1001-A 2015-03-19 16:14:00 348817157 RF Plant 6A Fast Interlock SR06/TI/EVR-CRF0602-A 2015-03-19 16:14:00 348817477 RF Plant 14B Fast Interlock SR14/TI/EVR-CRF1401-A 2015-03-19 16:14:00 348817590 RF Plant BO Fast Interlock BO04/TI/EVR-CRF1602-A 2015-03-19 16:14:00 348839036 BPMs Interlock - SR S16 SR16/TI/EVR-CDI1601-A 2015-03-19 16:14:00 348994600 BPMs Interlock - SR S09 SR09/TI/EVR-CDI0901-A 2015-03-19 16:14:00 349101458 BPMs Interlock - SR S13 SR13/TI/EVR-CDI1301-A 2015-03-19 16:14:00 349191712 BPMs Interlock - SR S08 SR08/TI/EVR-CDI0801-A 2015-03-19 16:14:00 349212879 BPMs Interlock - SR S04 SR04/TI/EVR-CDI0401-A 2015-03-19 16:14:00 349216442 BPMs Interlock - SR S01 SR01/TI/EVR-CDI0101-A 2015-03-19 16:14:00 349285449 BPMs Interlock - SR S15 SR15/TI/EVR-CDI1501-A 2015-03-19 16:14:00 349285585 BPMs Interlock - SR S03 SR03/TI/EVR-CDI0301-A 2015-03-19 16:14:00 349303126 BPMs Interlock - SR S07 SR07/TI/EVR-CDI0701-A 2015-03-19 16:14:00 349304615 BPMs Interlock - SR S05 SR05/TI/EVR-CDI0501-A 2015-03-19 16:14:00 349314670 BPMs Interlock - SR S10 SR10/TI/EVR-CDI1001-A 2015-03-19 16:14:00 349321386 BPMs Interlock - SR S11 SR11/TI/EVR-CDI1101-A 2015-03-19 16:14:00 349385919 BPMs Interlock - SR S06 SR06/TI/EVR-CDI0601-A 2015-03-19 16:14:00 349391899 BPMs Interlock - SR S02 SR02/TI/EVR-CDI0201-A 2015-03-19 16:14:00 349424265 BPMs Interlock - SR S14 SR14/TI/EVR-CDI1401-A 2015-03-19 16:14:00 349969651
06a (HVON, HVON) FIM: Timing, Revers Cavity, Forward Load EPS: no interlocks Tx01: FaultRfon {RFON is not enabled from EPS} Tx02: FaultRfon {RFON is not enabled from EPS} 06b (AUX, HVON) FIM: Timing, Revers Cavity, Forward Load EPS: no interlocks Tx01: not in operation Tx02: FaultRfon {RFON is not enabled from EPS} 10a (HVON, HVON) FIM: Timing, Revers Cavity, Forward Load EPS: no interlocks Tx01: FaultRfon {RFON is not enabled from EPS} Tx02: FaultRfon {RFON is not enabled from EPS} 10b (HVON, HVON) FIM: Timing, Revers Cavity, Forward Load EPS: no interlocks Tx01: FaultRfon {RFON is not enabled from EPS} Tx02: FaultRfon {RFON is not enabled from EPS} 14a (HVON, OFF) FIM: Timing, Revers Cavity, Forward Load EPS: IOT2_WF_ALRM Tx01: FaultRfon {RFON is not enabled from EPS} Tx02: not in operation
BACK

## Slide 37
BACK

## Slide 38
BACK

## Slide 39
BACK

## Slide 40
BACK

## Slide 41
BEAM CURRENT LOST
START
Example 3

## Slide 42
EPS
GUI
InfoTrip.py
PCGRID
Post Mortem
WHAT DO YOU WANT TO CHECK ?
What happened ?
NEXT
RF
GUI
General water cooling trend

## Slide 43
WHAT HAPPENED ?
RF Body Current
Beamline Ebutton
SR Kicker FAIL
SR Quad water ITLK
BPM FAIL
RF ARC CAVITY
CPCI REBOOT
SR Corr -> orbit -> Vacuum trip
SR QUAD CTRL FAILURE
Water cooling system fail

## Slide 44
End

## Slide 45
TRY AGAIN

## Slide 46
BACK

## Slide 47
Timing Log: Event description Device description Local time Timestamp [ns] RF Plant 10A Fast Interlock SR10/TI/EVR-CRF1001-A 2015-03-24 07:22:02 38882186 RF Plant 10B Fast Interlock SR10/TI/EVR-CRF1002-A 2015-03-24 07:22:02 70570819 RF Plant 6B Fast Interlock SR06/TI/EVR-CRF0601-A 2015-03-24 07:22:02 70714086 RF Plant 14B Fast Interlock SR14/TI/EVR-CRF1401-A 2015-03-24 07:22:02 70721651 RF Plant 6A Fast Interlock SR06/TI/EVR-CRF0602-A 2015-03-24 07:22:02 70727543 RF Plant 14A Fast Interlock SR14/TI/EVR-CRF1402-A 2015-03-24 07:22:02 70728008 RF Plant BO Fast Interlock BO04/TI/EVR-CRF1602-A 2015-03-24 07:22:02 70791131 BPMs Interlock - SR S02 SR02/TI/EVR-CDI0201-A 2015-03-24 07:22:02 71144544 BPMs Interlock - SR S06 SR06/TI/EVR-CDI0601-A 2015-03-24 07:22:02 71151941 BPMs Interlock - SR S11 SR11/TI/EVR-CDI1101-A 2015-03-24 07:22:02 71154999 BPMs Interlock - SR S01 SR01/TI/EVR-CDI0101-A 2015-03-24 07:22:02 71156889 BPMs Interlock - SR S07 SR07/TI/EVR-CDI0701-A 2015-03-24 07:22:02 71164342 BPMs Interlock - SR S12 SR12/TI/EVR-CDI1201-A 2015-03-24 07:22:02 71166871 BPMs Interlock - SR S03 SR03/TI/EVR-CDI0301-A 2015-03-24 07:22:02 71168168 BPMs Interlock - SR S13 SR13/TI/EVR-CDI1301-A 2015-03-24 07:22:02 71170050 BPMs Interlock - SR S16 SR16/TI/EVR-CDI1601-A 2015-03-24 07:22:02 71170866 BPMs Interlock - SR S16 SR16/TI/EVR-CDI1601-A 2015-03-24 07:22:02 71170882 BPMs Interlock - SR S09 SR09/TI/EVR-CDI0901-A 2015-03-24 07:22:02 71170930 BPMs Interlock - SR S10 SR10/TI/EVR-CDI1001-A 2015-03-24 07:22:02 71173508 BPMs Interlock - SR S08 SR08/TI/EVR-CDI0801-A 2015-03-24 07:22:02 71176414 BPMs Interlock - SR S15 SR15/TI/EVR-CDI1501-A 2015-03-24 07:22:02 71177999 BPMs Interlock - SR S04 SR04/TI/EVR-CDI0401-A 2015-03-24 07:22:02 71179904 BPMs Interlock - SR S05 SR05/TI/EVR-CDI0501-A 2015-03-24 07:22:02 71180193 BPMs Interlock - SR S14 SR14/TI/EVR-CDI1401-A 2015-03-24 07:22:02 71743991
06a (HVON, HVON) FIM: Revers Cavity, Forward Load, Timing EPS: CAV_WF_Outlet_ALRM Tx01: FaultRfon {RFON is not enabled from EPS} Tx02: FaultRfon {RFON is not enabled from EPS} 06b (AUX, HVON) FIM: Forward Load, Revers Cavity, Timing EPS: no interlocks Tx01: not in operation Tx02: FaultRfon {RFON is not enabled from EPS} 10a (STBY, STBY) FIM: Revers Cavity, Forward Load, Arc Watrax, Arc Cavity, Timing EPS: CAV_WF_Outlet_ALRM Tx01: FaultRfon {RF Reverse power interlock, RFON is not enabled from EPS} Tx02: FaultRfon {RF Reverse power interlock, RFON is not enabled from EPS} 10b (STBY, STBY) FIM: Forward Load, Arc Watrax, Arc Cavity, Timing EPS: no interlocks Tx01: FaultRfon {RF Reverse power interlock, RFON is not enabled from EPS} Tx02: FaultRfon {RF Reverse power interlock, RFON is not enabled from EPS} 14a (HVON, OFF) FIM: Revers Cavity, Forward Load, Timing EPS: IOT2_WF_ALRM Tx01: FaultRfon {RFON is not enabled from EPS} Tx02: not in operation
BACK

## Slide 48
BACK

## Slide 49
BACK

## Slide 50
BACK

## Slide 51
BACK

## Slide 52: Whishlist
52
Personal Safety System scada messages readable from the Control System
A “user oriented” EPS and MPS GUI:
  Different tabs from general view to detailed subsystem ITLKs
  Shows the logic with online data and alarm levels
  Integrates “save logs” and “reset” functions
  Integrates timing logs, RF FIM, …
In other words; a GUI that integrates the different tools to diagnose and recover the machine after a beam loss

## Slide 53: Questions?