## Slide 1: Status of the HLS-II Control System
Gongfa Liu
24 June 2019

## Slide 2: Outline
Introduction to Hefei Light Source
Overview of Control System
Development of Personnel Safety System
Plan for Post-Mortem System
Summary
2

## Slide 3: History of Hefei Light Source
Phase I
1984-1991
200MeV/800MeV
5 beam lines/end stations
Phase II
1998-2004
200MeV/800MeV
15 beam lines/end stations
More reliable/available
More beam lines/end stations
Upgrade Project
2009-2014
800MeV/800MeV
10 beam lines/end stations
HLS-II
Full energy injection
Lower emittance
More insertion devices
HALS？
(Hefei Advanced Light Source)
Notes: 本页PPT用来介绍各个阶段HLS的项目情况，以及现在HLSII所具有的参数；
3

## Slide 4: HLS-II
VUV and soft X-ray synchrotron radiation facility
0.8GeV, 66m, 38nm⋅rad, 360mA, top-off
5 IDs, 10 beam lines/end stations
Open since 2015, research projects >1200
Availability: >99% since 2016
Notes: 本页PPT用来介绍各个阶段HLS的项目情况，以及现在HLSII所具有的参数；
4

## Slide 5: HALS
Hefei Advanced Light Source
Project under proposal
Preliminary R&D is undergoing, supported by the Chinese Academy of Sciences and local government
Soft X-ray diffraction limited storage ring (DLSR) light Source
2.4GeV, 672m, 32cells,7BA, 23pm⋅rad, 300mA
Notes: 本页PPT用来介绍各个阶段HLS的项目情况，以及现在HLSII所具有的参数；
5

## Slide 6: Hardware Structure of Control System

## Slide 7: Hardware Components
Server Platform: VMware vSphere
  Physical Machine: 4 DELL PowerEdge R710
  Virtual Machine: > 40, test and development platform, file server, database server, web server, softIOC
  Storage: iSCSI SAN, RAID
OPI: 5 Linux/PC + 1 virtual server, NIS
Screen Wall: 3*4 55″ LED screen
Front end controller
  cPCI: 5, timing system
  PLC: 8, IDs, vacuum valve etc.
  NI cRIO 9073: 20, temperature monitor
7

## Slide 8: Central Control Room
8

## Slide 9: Software Design
Development tools: EPICS
  base：R3.14.12.2
  modules：seq-2.1.6, asyn4-18, streamDevice-2-5, s7plc、tds3000-2.4, iocStats-R3-1-9, autosave-4-7
  Extensions：edm-1-12-75, SNS_CSS_3.1.4, pyepics-3.2.0, procServ
Operating system
  Server/OPI：CentOS 6
  SoftIOC：CentOS 6
  NI cRIO 9073: vxWorks
IOC：～15,000 records
Database
  RDB Channel Archiver＋ Oracle＋JSP
  History data:～15GB/week
Programming Language
  C/C++, Java, MATLAB, Python, LabVIEW

## Slide 10: Timing System
Hardware
  cPCI controller: 5
  MRF cPCI modules
    EVG300: 1
    Fanout12: 1
    EVR300: 8
    EVRTG300: 4
Software
  OS: CentOS 6
  IOC Device/Driver Support
    General record type: ai, ao, bi, bo, mbbi and mbbo
    Developed by ourselves
Performance
  Jitter: 180ps (peak to peak), 27ps (stdev), within 24h

## Slide 11: Layout of Timing System

## Slide 12: HLA(High Level Application)
Feature
  Physics Quantities Based Control
  A softIOC is used for the conversion between Engineering Quantities and Physics Quantities

## Slide 13: Conversion Diagram
13

## Slide 14: Archiver System
14
Data Archiver
  RDB Channel Archiver: Oracle
  Python Scripts: SQLite，Data file
  Java Channel Access: IOC
Data Retrieval
  Front end: Vue.js
  Back end: Spring Boot
  Web server: Nginx
  Functions
    Operation status
    Historical data query: customized, free
    Data analysis
    Radiation dose monitor
    PSS (Personnel Safety System) access information

## Slide 15: Structure of Archiver System
15

## Slide 16: Operation Status
16

## Slide 17: Data Query: Customized
17

## Slide 18: Data Query: Free
18

## Slide 19: Alarm System Based Phoebus/Alarms

## Slide 20: Web Based GUI of Alarm System

## Slide 21: Alarm Messages Distributed by SMS& WeChat
SMS: Failure Message Recovery Message
WeChat: Failure Message Recovery Message

## Slide 22: Personnel Safety System (PSS)
Upgrade Background
  The existing system is based SiPASS, turn-key mode
    Not easy to maintain
    Can not share info
  Add the function of personnel management
Development
  Hardware
    Redundant PLC: Siemens S7-412-5H
    PROFINET
  Software
    EPICS
    IOC Driver for Redundant PLC
Offline Test：has worked well since Mar. 2019
To be installed in Aug. 2019

## Slide 23: System Architecture of PSS
EPICS IOC/OPI
Redundant PLC
Front Device
  IO Station：14
  Door: 14
  Input Signal: 149
  Output Signal: 46

## Slide 24: Photo of PSS Test Platform

## Slide 25: Control Panel of PSS

## Slide 26: Control Panel of PSS: Linac

## Slide 27: Control Panel of PSS: Ring

## Slide 28: Info Screen of PSS Beside the Door

## Slide 29: Access Information of PSS

## Slide 30: Post-Mortem System（PM）
Important tool to analyze the cause of beam trip
PM Components
  Generation and distribution of the trigger signal
  Storage of relevant signals
    RF, BPM, PS, etc.
  Data Recorder
    BPM platform, Oscilloscope, Data Recorder, etc.
Our Plan
  YOKOGAWA DL850E ScopeCorder
  Update the timing system to distribute the trigger signal
  …

## Slide 31: Architecture of PM
YOKOGAWA DL850E ScopeCorder
  8 input module slots
  Up to 128 channels
  Up to 100 MS/s sampling rate
  Up to 16-bit analog resolution

## Slide 32: Summary
The control system has been put into operation since 2015
  Failure Time: 2.5 Hours totally
  Stable and Reliable
Use virtualization technology to build the server system
Try to use the software existing in the EPICS community as much as possible
Make development based on the existing software, e.g. the timing system, the alarm system, etc.
Minimize the kinds of hardware and software
Develop the new PSS with EPICS, redundant PLC and PROFINET
Plan to set up the post-mortem system

## Slide 33
Thank You！